# SECTION VI: SPECIFICATIONS

## KIWA AND KIBWONGI ISLANDS SOLAR MINI-GRID SPECIFICATIONS

PART I

Power Plant Specifications

- General Description

Rural Electrification and Renewable Energy Corporation (REREC) invites eligible bidders to participate in the design, supply, installation, testing, and commissioning of two solar mini-grids in Homabay County: a 120kWp solar PV-Diesel hybrid plant on Kiwa Island and a 60kWp solar PV-Diesel hybrid plant on Kibwongi Island

- Project Location

The off-grid solar Photovoltaic (PV) Power Plant to be supplied and set to work under this contracts shall have an output of not less than 60 kW and 120Kw at the point of the Inverter Output. The plants shall be installed in Kiwa and Kibwongi Islands in off-grid county of Homabay.

Annex 1.

The document has tender for design, supply, testing and commissioning of a 2No. Solar Minigrids complete with their solar modules, Hybrid inverters, Lithium ion Phosphate batteries, intelligent controller/manager, mounting support, electrical controls, protection and instrumentation, a diesel generator backup and Step up substation (0.415/11KV) complete with all associated accessories and civil works.

- System Description

During the daytime, the Solar Power Generation Plant should supply power directly to the Loads in online mode, along with charging of the batteries in continuous mode. On most non-cloudy days during the year (“regular day”), batteries should get fully charged during the day time. In evening or morning (Sun period) battery should support the Solar Power Generation Plant to meet the load, if required

The solar PV hybrid power plant shall consist of the following main components:

  - Solar PV modules

  - Solar PV modules structures

  - Hybrid inverters

  - lithium ion batteries

  - Diesel thermal generator for reserve power

  - Switchgear

  - Step up substation (0.415/11 KV)

  - Outdoor sub-station equipment

The tenders are for design, supply and commissioning of a new solar PV hybrid generation plant complete with its solar modules, inverter, lithium ion phosphate batteries with battery rack, diesel thermal generator with automatic startup function, mounting structure for modules, electrical controls, protection and instrumentation and Step-up substation (0.415/11KV) complete with all associated accessories and civil works. The plants shall be installed at the Kiwa and Kibwongi islands in Homabay County, Suba South Constituency.

The solar PV power plant is also equipped with a Diesel Generator, which shall be used normally as reserve power. The diesel generator should switch on automatically whenever the state of charge of the battery reaches a set depth of discharge. This will be defined at commissioning stage. The diesel generator shall be sized to charge the lithium ion batteries so that the power plant is operating at its optimum power rate. The diesel generator shall comprise a 50kVA unit in three-phase operation. The diesel generator has to be equipped with automatic startup function controlled by a robust energy management system (EMS). The priority has to be given to use the solar energy and the diesel generator will meet the energy deficit. In case of a power outage of the inverter, the critical loads have to be bypassed to the diesel generator by manual switch over.

The battery bank shall be charged by solar power during the day and its capacity shall be determined with C10 capacity rate.

3.1 Description of Electrical Components and Requirements

- Solar PV Modules

  - SPV Mono crystalline modules of minimum 72-cells; and minimum 22% module efficiency.

  - Solar modules offered shall be;

    - Tier-1 Manufacturer

    - Certified as per IEC 61215

    - Qualify IEC 61730- Part -1: PV Module Safety Qualification Part -1 Requirement for Construction.

    - Qualify IEC 61730- Part -2: PV Module Safety Qualification Part -2 Requirements for Testing.

  - As SPV modules shall be used in highly corrosive atmosphere throughout their life time so they must qualify IEC 61701.

  - Solar PV Module design shall conform to following requirement:

    - Weather proof, DC rated MC4 connector and a lead cable coming out as a part of the module, making connections easier and secure, not allowing any loose connections.

    - Resistant to water ingress, abrasion, hail impact, humidity, sea water & other harsh environmental factors for the worst situation at site.

  - Module rating is considered under standard test conditions; however Solar Modules shall be designed to operate and perform under site conditions including high temperature, dusty conditions, high humidity and corrosive atmosphere.

  - Identification and Traceability:

Each PV module shall have Radio Frequency Identification (RFID) Tag. The following information must be mentioned in the RFID used on each module. This can be inside or outside the laminate but must be able to withstand harsh environmental conditions.

    - Name of the manufacturer of SPV module.

    - Name of the manufacturer of Solar cells.

    - Month and year of the manufacturer (separately for solar cell and module).

    - Country of origin (separately for solar cell and module).

    - I-V curve for the module.

    - Peak wattage, Im, Vm and PF for the module.

    - Unique Serial No and Model No of the module.

    - Date and year of obtaining IEC SPV module qualification certificate

    - Name of the test lab issuing IEC certificate other relevant information on traceability of solar cell and module as per ISO 9001and ISO14001.

  - Any other markings as required in the specifications shall also be made on the modules.

  - Warranties for Modules:

Product Warranty The manufacturer should warrant the solar module(s) to be free from the defects and/or failures specified below for a period not less than ten (10) years from the date of sale to the original customer (“Employer”)

    - Defects and /or failures due to manufacturing.

    - Defects and/or failures due to quality of materials.

    - Non-conformity to specifications due to faulty manufacturing and/ or inspection processes.

  - Performance Warranty

    - A 25-year long-term performance warranty with a maximum linear decrease in peak power at STC of 2.5% in the first year, 0.6%/year in subsequent years. At year 25, the peak power shall be not less than 83%.

    - Bidder shall provide data sheet for solar PV module (under standard testing condition) along with their offer as per Guaranteed Technical Particular.

- Module Mounting Structure (MMS)

  - The MMS to be used for mounting the SPV modules shall be as under:

    - Fixed-tilt type.

    - Azimuth: 0º True South/North.

    - Tilt angle: 10º -15º tilt angle shall provide for all sites with adequate spacing to prevent inter row shading.

    - Structure shall comply with IEC 61215/61646.

  - The mounting steel structure and its galvanizing shall be as per the required standards.

  - The mounting structure shall be suitably designed for mechanical and electrical installation. It shall support SPV modules at a given orientation, absorb and transfer the mechanical loads along with applicable wind loads to the base properly.

  - While designing of MMS additional care is needed to ensure that the material size used is capable to withstand the wind forces generated on account of heavy wind speed of respective sea wind zone. MMS with documented results of wind tunnel testing and resonant frequency dampening is preferred.

  - To reduce the pressure on structure and foundation, clear spacing between two adjacent modules shall be sufficient to allow wind passage.

  - The minimum clearance between the lower edge of the modules and developed ground level shall be adequately elevated above relevant flood plain. Minimum 1000 mm or higher and to employer’s approval.

  - Contractor has to choose suitable foundation design(s) depending on soil conditions, geographical condition, regional wind speed, bearing capacity, slope stability etc.

  - The structure shall be designed to allow easy replacement of any module.

  - Spacing between rows shall be so designed that shadow of one row of modules to next is avoided.

  - The Contractor (successful bidder) shall furnish detailed design calculation.

  - Nut & bolts, supporting structures including module mounting structures shall have to be adequately protected against all climatic conditions prevailing in the area.

  - All fasteners shall be of stainless steel of grade SS 304 or suitable equivalent.

  - The mounting structure shall be grounded properly using maintenance free earthing kit.

  - The mounting structure & foundation shall be designed to withstand applicable speed of wind zone of the applicable site as given in relevant International/Kenya wind load codes / standards. Suitable fastening arrangement such as grouting and clamping should be provided to secure the installation against the specific wind speed. The contractor shall ensure that the design has been certified by a recognized lab/ institution in this regard and submit the same to the Employer.

- Array Junction Boxes (AJB)/String Monitoring Box (SMB)

  - To receive the DC output from field array, junction box / string monitor Box (SMB) as per design requirement shall be provided in between solar array and DCDB/PV Inverters. They shall be rated for 600/1000V and comply with IEC61439-2, UL1741 and standards.

  - AJB can also be integrated into Inverter for space saving.

  - AJB having polycarbonate enclosure of dust & vermin proof shall conform to IP 65 protection.

  - Array junction box allows several PV strings to be connected in parallel.

  - Suitable capacity MCBs/MCCB shall be provided for controlling the DC power output to the inverter along with necessary surge arrestors.

  - A DC dis-connector switch must isolate the array DC circuit as per requirement

- DC Distribution Board/DC combiner box

  - To receive the DC output from junction box /string monitor box (SMB) as per approved design requirement DCB to be provided in between JCB/SMB and PV inverter. They shall be rated for 600/1000V and comply with IEC61439-2, UL1741 and standards.

  - Sufficient no. of switchboards / DC DB wherever required shall be provided.

  - DCDB should be equipped with appropriate functionality, safety (including fuses, grounding, etc.) and protection.

  - The terminals will be connected to bus-bar arrangement of proper sizes to be provided. The panels/ boxes will have suitable cable entry points fitted with cable glands of appropriate sizes for both incoming and outgoing cables.

  - DC DB enclosure of dust & vermin proof shall conform to IP 65 protection if out door.

  - DC DB allows requisite connections from JB/SMB to be connected in parallel.

  - Suitable capacity MCBs/MCCB shall be provided for controlling the DC power output to the PV inverter along with necessary surge arrestors.

  - DC DB shall be provided with the purpose of providing option for isolating the battery bank.

  - There shall be copper bus bars of desired size/rating and can either be independent or integrated in PSU.

  - A DC dis-connector switch in DCDB must isolate the array DC circuit as per requirement

- Hybrid Inverter integrated with MPPT Charge Controller

The hybrid Inverter Unit shall be hybrid Inverter with power exporting facility to the Grid.

  - All the Inverters should contain the following clear and indelible Marking Label & Warning Label as per IS16221 Part II, clause 5. The equipment shall, as a minimum, be permanently marked with:

    - The name or trademark of the manufacturer or supplier.

    - A model number, name or other means to identify the equipment.

    - A serial number, code or other markings allowing identification of manufacturing location and the manufacturing batch or date within a three-month time period.

    - Input voltage, type of voltage (A.C. or D.C.), frequency, and maximum continuous current for each input.

    - Output voltage, type of voltage (A.C. or D.C.), frequency, maximum continuous current, and for A.C. outputs, either the power or power factor for each output.

    - The Ingress Protection (IP) rating

  - The Hybrid inverter output shall be 415 VAC, 50 Hz, 3 phase.

  - The Hybrid inverter should have all the technical requirements for connecting to the Grid and provision of Intentional Islanding with facility for connecting to a battery bank

  - The Hybrid inverter shall include appropriate self-protective and self-diagnostic feature to protect itself and the PV array from damage in the event of inverter component failure or from parameters beyond the inverter’s safe operating range due to internal or external causes.

  - Maximum Power Point Tracker (MPPT) shall be integrated into the inverter to maximize energy drawn from the solar PV array. MPPT shall be microprocessor/micro controller based to minimize power losses and maximize energy utilization. The details of working mechanism of MPPT shall be mentioned by the Bidder in its proposal. The MPPT unit shall confirm to IEC 62093 for design qualification.

  - The Inverter shall always give preference to Solar power, and will use BESS power only when the solar power is unable to meet the loads requirement

  - Inverter should comply with IEC 61683 for efficiency and measurements and should comply with IEC 60068-2 for environmental testing.

  - The efficiency of the inverter shall be more than 95% at full load. The inverter shall have high overload capacity. The Bidder should specify the overload capacity in the bid.

- Battery Energy Storage System (BESS)

  - Supply of Battery Energy Storage System (BESS) with Lithium-ion Battery pack, conforming to IEC62619 standards with warranty of 5 years, 6,000 cycle’s minimum. Complete in all respects as under and confirming to Employer’s Requirement & technical specification, consisting of;

    - Lithium-ion Battery Power Packs for required energy capacity, or equivalent as per approved design, minimum 80% Depth of Discharge (DOD) for Lithium-Ion. Batteries should be capable of at least C/4 charge and discharge rate.

    - Enclosures confirming to IP35 for Indoor /IP65, or better for outdoor.

    - All accessories for correct installation, foundation, connection, controls, and operation of BESS.

  - The battery storage shall be Lithium Iron Phosphate (LFP) type and shall be installed in a well-insulated and air-conditioned room or container.

  - Warranted number of cycles for the BESS at the supplier recommended depth of discharge                            should not be less than 6,000 cycles at full DOD indicated by the battery manufacturer specifications.

  - The battery warranty should be 5 years minimum. If due to any reason battery is required replacement, then the Contractor is to replace the same in warranty period without any extra cost to the Employer.

  - System voltage of above 48V. All equipment to have matching voltages to the existing system voltage

  - Suitable number of corrosion resistant and acid-proof storage racks shall be supplied to accommodate the cells, testers and other accessories. The rack design shall be such that minimum space is required, without any way obstructing the maintenance requirements. For metallic racks, standards specified for control panel enclosures and other metallic shall govern.

  - There shall be no environmental hazards caused due to:

    - Improper use and maintenance of the battery bank.

    - Improper disposal of batteries at the time of replacement.

    - Any manufacturing defects.

  - All technical and other details pertaining to the storage cells shall be supplied including but not limited to the following:

    - Rated voltage and ampere-hour capacity of each storage cell as the rated discharge  rate,

    - Permitted maximum DOD,

    - Self-discharge rate

    - Cycle life of the storage cell and the anticipated life (in years) of the battery bank.

    - Total number of storage cells in use.

    - Details on cell interconnections, if any

    - Charging system used for battery

  - The system should allow for the load current to be supplied at the same time as the battery charging current.

  - The contractor shall submit (in 4 sets) complete design and expected performance of BESS Calculation, drawings, reports and data for approval of the Employer during detailed engineering.

  - The design of BESS with critical parameters such as response time discharge duration, Depth of Discharge, frequency of discharge, cycle life, round trip cycle efficiency performance degradation, self-discharge characteristics, short time discharge rating, transient response characteristics, auxiliary system requirement etc shall be included in the detailed engineering.

  - Suitable Fire protection and suppression system shall be designed for BESS in line with IEC or international requirements/specifications regulation as applicable and system requirement considering project site. BESS to be housed in one room in the control room/building. The battery room shall have an automated fire detection, prevention and suppression system fitted with a dry aerosol agent to put out Lithium-Ion battery fires. The system shall include smoke detectors, horn strobes and other components required to enable it function properly and suppress fires while preventing unintended release.

  - BESS confirming to International Safety and Electrical Standards shall be Complete in all  respect consisting of:

    - Complete with programmable control and regulation parameters, protection system, control system, surge protection system etc.

    - Requisite numbers of battery pack, the combination of which shall equal or exceed the estimated capacity shown in design characteristics in this document, with Minimum. 80 % DOD,

    - Enclosures conforming to IP35 for Indoor.

    - All accessories and connection for correct installation and operation of BESS.

    - All cables for inter connection with main AC distribution board.

    - Support structure to keep batteries at a suitable clearance level from ground to take care of water flooding etc. The design shall be submitted to the employer before its implementation.

    - Test certificate and test reports as per IEC62619 standard applicable to battery technology shall be submitted for approval of the Employer. All other test certificate and test reports as per international standards and requirements/specifications for large scale BESS shall be submitted for approval of the Employer during submission of detailed engineering.

  - Suitable protection/isolation for the battery system should be provided with proper rating of 40 fuses and isolators for DC application. This should be connected between battery bank and battery inverter/charger.

3.1.6 	Diesel Generator

The Diesel Generator shall have a 3-phase 50KVA power output with 415 V at 50 Hz. It should include a highly corrosion resistant enclosure, control panel and monitoring, fuel tank and circuit breaker protection. The diesel generator shall be suitable for outdoor installation and perform accordingly with the battery inverter and the system design. The diesel generator shall work in a fully automated manner with the above stated component. A concrete plinth to be constructed for the generator placement plus a shed of steel hollow sections and IT 4 sheets to engineer’s approval to house the generator.

3.1.7 	Data Monitoring

In order to achieve a high performance of the solar PV hybrid power plant, the incorporation of automatic data acquisition and monitoring technology is essential. This allows that the yield of the PV plant can be monitored easily and compared with calculations made from solar irradiation data to raise warnings on a daily basis in case of a shortfall. Important information on for example State of Charge of the battery storage and other relevant energy and power value from the system including time stamps of diesel generator operation can be detected and rectified before they have an appreciable effect on system performance. A data monitoring system shall be installed to meet the requirements above and has to give the opportunity to receive the system data via GSM and to allow remote access to the solar PV hybrid power plant. The electrical power supply of the data monitoring system shall be from DC power of the battery. Corresponding electrical adaption of the monitoring to the DC power supply level shall be installed.  Remote monitoring and data acquisition through Remote Monitoring System Software at the REREC location with latest software/hardware configuration and service connectivity for online / real time data monitoring complete to be supplied by the supplier. Provision for interfacing these data on REREC server and portal in future shall be kept. Reliable sensors for solar radiation, temperature & other electrical parameters are to be supplied with the data logger unit. Communication interface the entire system can be operated and monitored via various interface viz (RS232, RS485, MPI, Profit-bus, Telephone modem), in addition to the information indicated on the operator panel. Remote Monitoring may be achieved directly via inverter interface or via third party data acquisition system. Remote monitoring system should allow for rudimentary parameter adjustment.

3.1.8 Lightning & Over Voltage Protection

- The Solar plant shall be provided with lightning and over voltage protection connected to proper earth pits. Earthing pits shall be measured to have an earthing resistance of 1Ω or less at the time of installation. If this level cannot be obtained with the soil at the facility, then soil conditioning (engineered backfill) shall be implemented to improve the earthing resistance within acceptable levels.

- The main aim of over voltage protection is to reduce the over voltage to a tolerable level before it reaches the PV or other sub-system components as per NFC 17-102. The source of over voltage can be lightning or other atmospheric disturbance.

- Lightning mast/conductor, placed at strategic locations, shall be used to protect the arrays against lightning protection. The bidder shall give detailed design showing location of lightning conductor/masts and the protection coverage on array without causing any shadow on the modules to the Employer.

- All design shall be submitted to the Employer before its implementation.

- Necessary concrete foundation for holding the lightning conductor in position to be made after giving due consideration to maximum wind speed and maintenance requirement at site in future.

- The lightning conductor shall be earthed through GI flats and connected to with earth pits per applicable International Standards. Three earth pits shall be provided for each lightning arrestor. Each lightning conductor shall be fitted with individual earth pit as per required Standards including accessories, and providing masonry enclosure with cast iron cover plate having locking arrangement, watering pipe using charcoal or coke and salt as required as per provisions of IS.

- Design calculations, technical specification and requisite test reports of lightning mast conforming to international standards along with detailed write up in 4 sets shall be provided for approval to the Employer.

3.1.9 Earthing Protection

- Earthing system shall be in strict accordance with IEC specified and applicable Electricity Rules / Acts and Guidelines for connections.

- Earthing system network / earth mat shall be of interconnected mesh of GI flats buried in ground in the plant. The interconnections shall be done with GI flats of suitable sizes. The earth conductors shall be free from pitting, laminations, rust, scale and other electrical, mechanical defects.

- Metallic frame of all electrical equipment shall be earthed by two/three separate (as per KPLC norms) and distinct connections to earthing system, each of 100% capacity, with the exception of solar panels, for which alternate means of code-compliant earthing shall be admissible if integrated with racking design.

- Metallic sheaths / screens, and armor of multi-core cables shall be earthed at both ends. Metallic sheaths and armor of single core cables shall be earthed at switchgear end only unless otherwise approved.

- Each continuous laid lengths of cable tray shall be earthed at minimum two places by G.S. flats to earthing system, the distance between earthing points shall not exceed 30 meter/ KPLC norms. Wherever earth mat is not available, necessary connections shall be done by driving an earth electrode in the ground.

- Neutral connections and metallic conduits/pipes shall not be used for the equipment earthing.

- Lightning protection system down conductors shall be terminated to separate earth electrodes & not be connected to other earthing conductors.

- Connections between earth leads and equipment shall normally be of bolted type. Contact surfaces shall be thoroughly cleaned before connections. Equipment bolted connections after being tested and checked shall be painted with anti-corrosive paint / compound.

- Back filling material to be placed over buried conductors shall be free from stones and harmful mixtures. Back filling shall be placed in layers of 150 mm.

- Earth pit shall be constructed as per IEC standard specified, Minimum spacing between electrodes shall be 2000 mm. Earth pits shall be treated with salt and charcoal/chemical Powder Earthing.

- Earth resistance at earth terminations shall be measured and recorded. All equipment required for testing shall be furnished by successful bidder.

- Each array structure of the SPGP yard/shed shall be grounded properly as per standard.

- The Array Structure is to be connected to earth pits as per standards. Junction boxes shall be connected to the main earthling conductor/electrode.

- The arrays shall be in protected zone of lightning arrester/spheres by installation of suitable lightning surge diverters/arrestors. The earth electrodes for the same shall have to be completely separate from the plant/array earthing.

- All metal casing/shielding of the plant shall be thoroughly grounded in accordance with applicable electricity act/rules/guidelines. Total earthing system installation shall be in strict accordance with the latest editions of Electricity Rules, relevant Standards and code of practices and the local statutory authority regulations.

- Necessary test point provision shall be made for bolted isolating joints of each earthing pit for periodic checking of earth resistance.

- All non-current carrying metal parts shall be earthed with two separate and distinct earth continuity conductors to an efficient earth electrode.

- Earthing Design And Layout

- The successful bidder shall submit Design along with drawings showing the location of lightning arresters and protection zones to cover all arrays against lightning for approval from Employer.

- The earth mesh system design consisting of G.I Flat shall be submitted for approval of Employer.

- Total plant earthing system shall be designed to give an earth resistance of less than 1 ohm all along the earth mesh.

- Earthing conductors in outdoor areas shall be buried 1.5 to 2M below finished graded level and these buried conductors shall be brought 500 mm above ground level for making tap connections to the equipment.

- All the electrodes shall be 50 mm diameter GI pipe, 3.0 m long and shall strictly be as per IS: 3043/IEC of latest revision.

- Each phase of lightning arrestor shall be earthed through GI flat (considering salty weather) connected to an individual earth electrode.

- If present, air break switches and DO fuses shall also be earthed GI flat to the main earthing flat.

- Metallic conduits and pipes shall not be used as earth continuity conductor.

- GI conductors shall be provided for earthing the lighting fixtures, receptacles, junction boxes, lighting conduits and this conductor in turn shall be connected to the main earthing conductor / electrode.

- Equipment Housing

4.1.1 	Power House

The Multi-Mode Inverter (hybrid), data monitoring equipment, and all monitoring equipment shall be installed indoors with equipped Air conditioner and fire suppressing Unit according to the equipment manufacturer’s recommendations. All electrical boards and LV protections will also be installed indoors. The battery storage shall be installed indoors in a separate room equipped also with Air Conditioner and fire suppressing unit according to the equipment manufacturer’s recommendations. All recommendation and regulations for installing the selected batteries in has to be taken into account. The Diesel Generator shall be installed outdoors.

The Power House shall also be equipped with safety and protective elements required for operations, maintenance and emergencies. This will include fire extinguisher, water source, protective goggles and clothing, etc.

- Air Conditioner is a must for all rooms / compartments in the Power House.

- “Double Layer Roof” to reduce heating room from direct sunlight.

- Outer roof layer must be big enough to avoid direct sunlight heating technical rooms / compartments, over the course of the year.

- Insulated walls to reduce outside heat energy flow

4.1.2 	Housing Solution

The inverters and all monitoring equipment shall be installed with Air conditioner according to the equipment manufacturer’s recommendations in a standard structure and the tenderer to submit with the bid document detailed design of the structure which will house all the equipment and present for approval. The structure has to be delivered and placed on reinforced concrete blocks by the tenderer. The Structure shall be further placed under an open shed made of steel hollow sections and IT4 sheet roof so that direct sunshine does not fall on structure and there is adequate space between the shed and Structure to allow air circulation. The place has to be appropriate and protected from lightning. Location has to be chosen that no heavy rain or seasonal flooding can enter the structure. Foundation above ground has to be minimum 2 steps, each 14 cm.

Thermal insulation inside the structure is advised. Proper wall mounting support for Inverter and AC distributions is advised. Pre-installed Inverter and other equipment is not recommendable. Preinstalled equipment will lead to loss of manufacturer warranty as damage may occur due to transport (shaking). Pre-installed battery is not possible due to safety regulations.

The inverters installed under the solar panels mounting with a small shed above to reduce risk of rain/water on the inverter but with adequate room for air circulation to reduce temperature build-up. The inverters shall have protection of at least IP54

4.2.1 	Electrical Protection

The solar PV hybrid system shall contain all necessary electrical protection to ensure the safety of persons and goods. At the LV distribution boards, thermomagnetic circuit breakers with C trip curve shall be included meeting IEC 60947-2 requirements. It shall also be included differential residual current circuit breaker for the person protection (RCD).

It is also important to implement a lighting protection system, ensuring the coverage of the whole PV plant, Power House, Container and Diesel Generator. Installation & Commissioning by approved / certified / licensed company.

4.2.2 	Transmission and Distribution Line

The electricity distribution from the generation plant to the end consumers will be done by means of a distribution line formed by a Medium voltages (MV) line at 3-phase 11 KV/ 50 Hz. This will be done in a separate scope from this tender.

The power from the solar plant shall be connected to the electrical system of REREC through a 500 amps breaker and isolator of the same capacity to be provided by the tenderer. The tenderer shall also provide  and install an energy tariff meter complete with current transformers (CTs) for measuring energy generated by the solar PV hybrid power plant and .

##### 4.3 Balance of System

The Balance of System (BOS) encompasses all components of a solar PV hybrid power plant that includes wiring, switches, a mounting system, and one or many inverter battery bank. BOS refers to all components of a PV system other than the modules. In addition to inverters and racking, this includes

##### 4.5 General Rating

The solar PV hybrid power plant has to be capable of producing the maximum output under the continuous ambient temperatures, altitude and relative humidity given below:

Temperature:  	Max. 45 degrees Celsius

Min. 18 degrees Celsius

Average 32 degrees Celsius

Relative humidity: 	90 – 100 %

4.6 Cables & Wiring

All instruments and panel wiring shall be of heat resisting and self-extinguishing type in compliance with IS.  Plastic or porcelain cleats of the   limited compression type shall be used for holding wiring runs.  All wires shall be suitable for bending to meet the terminal studs   at right angles.  Metal cases of all apparatus mounted on panels shall be separately earthed by means of copper wire or strips.

The following color scheme of the wiring shall be used as per standard for three phase systems.

a)   AC three phase circuits:

- No.1 Phase         		: Red.

No.2 Phase         		: Yellow.

No.3 Phase         		: Blue

- Neutral conductor 		: Black

- Connection to earth	  	: Green

b)   D.C. circuits

- Positive			:Red

- Negative			:Black

4.7 Cables and Accessories

Cables of appropriate size to be used in the system shall have the following characteristics:

  - Shall meet IEC 60227/IS 694, IEC 60502/IS1554 standards

  - Temp. Range: –100C to +800C

  - Excellent resistance to heat, cold, water, oil, abrasion, UV radiation.

  - Flexible.

  - Sizes of cables between array interconnections, array to junction boxes, junction boxes to inverter etc. shall be so selected to keep the voltage drop (power loss) of the entire solar system to the minimum. The cables (as per IS) should be insulated with a special grade PVC compound formulated for outdoor use.

All the cables shall conform to the requirements of the related standards and codes for:

  - DC cable for photovoltaic system

  - XLPE / PVC insulated (heavy duty) electric cables for working voltages up to and including 1100V.

  - Recommended current ratings

  - Low carbon galvanized steel wires, formed wires and tapes for armoring of cables

  - VC insulation and sheath

  - Cross linked polyethylene insulated PVC sheathed cables

  - Conductors for insulated electrical cables and flexible cords.

  - Standard test method for density of smoke from the burning or decomposition of plastics.

  - Tests on gases evolved during combustion of electric cables.

  - Tests on electric cables under fire conditions.

5. 	Main Technical Specification of Solar PV Hybrid Power Plant

Table 1 summarizes the required main technical specification of the solar PV hybrid power plants.

| Pos 1 | General Specification |  |  |
| --- | --- | --- | --- |
| 1.1 | Name of project site | Kiwa islands solar mini grid | Kibwongi islands solar mini grid |
| 1.2 | Coordinates |  |  |
| 1.3 | Site altitude |  |  |
| 1.4 | Daily load demand | 500 kWh/day | 500 kWh/day |
| 1.5 | Annual yearly demand rising for the next 5 years | 3 % | 3 % |
| 1.6 | Renewable Energy fraction | 90 % | 90 % |
| Pos 2 | Solar PV Generator |  |  |
| 2.1 | Solar PV Generator Capacity (Minimum) | 120KWp | 60KWp |
| 2.2 | Module type | Silicon monocrystalline (Mono PERC) | Silicon monocrystalline (Mono PERC) |
| 2.3 | Module nominal power | >400 W |  |
| 2.4 | Inverter type | Hybrid inverter | Hybrid inverter |
| Pos 3 | Battery Storage |  |  |
| 3.1 | Battery type | Lithium-Ion type | Lithium-Ion type |
| 3.2 | Battery String Voltage | => 500 V DC | => 500 V DC |
| 3.3 | Battery Usable Capacity | 361KWh | 181KWh |
| 3.4 | Battery cycles | 6000 at 80% DOD @25℃ | 6000 at 80% DOD @25℃ |
| Pos 4 | Diesel Generator |  |  |
| 4.1 | Fuel type | Diesel | Diesel |
| 4.2 | Generator type | Synchronous generator | Synchronous generator |
| 4.3 | Generator power output | 3-phase | 3-phase |
| 4.4 | Number of generators | 1 | 1 |
| 4.5 | Rated power | 50 kVA | 50 kVA |
| 4.6 | Start behavior | Automatic-startup | Automatic-startup |
| Pos 5 | AC distribution line (To be done by REREC) |  |  |
| 5.1 | Distribution type | Medium voltage 11KV | Medium voltage 11KV |
| 5.2 | Frequency | 50 Hz | 50 Hz |
| 5.3 | Number of LV transformer |  |  |
| Pos 6 | Data Monitoring system |  |  |
| 6.1 | Energy and power values from solar PV power plant | 1No. | 1No. |
| 6.2 | Data from battery management | 1No. | 1No. |
| 6.3 | Digital energy tariff meter for the Trading Centre Out Put | 2No. | 2No. |
| 6.4 | Control Panel for Energy and power values from Diesel Generator) | 1No. | 1No. |
| 6.5 | GPRS/ GSM Modem for remote assess | 1No. | 1No. |
| 6.6 | Meteorological sensors (solar radiation, ambient temperature, wind speed) | 1No. | 1No. |

Table 1: Required technical specification of the solar PV hybrid power plants

6. 	Documentation

All work steps will be documented in detail throughout the construction phase. The documentation will include as build plans, datasheets, technical specifications, and installation and operation manuals for each component of the installed system.

##### 6.1 Operation & Maintenance Manuals

One (1) original and two (2) copy sets (hard and soft copies) of comprehensive operating and maintenance manuals bound in hard covers shall be supplied prior to handing over the plant to the employer. The manuals shall detail out the operating regimes and critical settings and tolerance to be maintained during inspection of the plant. The O & M manuals will be provided after completion of the installation.

##### 6.2 Drawings

The tenderer shall submit together with the tender document drawings and parts identification lists for every item of the plant together with a full list of all sub-contractor’s addresses fax numbers, emails, etc. The drawings shall contain exploded views/diagrams of the main assemblies comprising the plant together with a means of identifying each component including its part number, reference and description as per the manufacturer’s coding system. The contractor’s coding system shall not be acceptable.

The tenderer shall submit with original and two copies of his tender general arrangement drawings and typical details of the essential items of the plant offered which will be used in during the erection period.

All drawings shall be submitted folded to A4 size with the drawings box visible on the outside. After commissioning the plant, two sets of as built drawings will be handed over to the Employer, which shall include but not limited to:

- General arrangement drawings, assembly drawings, pipe work layouts, terminal point details, foundation and erection drawings.

- Single line logic diagrams for all control systems and main electrical systems

- Wiring and pipe work diagrams, interconnection diagrams and schematic diagrams for equipment modules and systems.

After award of the tender, discussions will be held with the employer on the drawings submitted with the tender that will lead to final approval of the drawings by the employer.  Before the final approval, the drawings shall be modified as necessary if requested by the employer.

The taking over certificate will not be issued until the built drawings, O&M manuals and catalogues have been submitted and accepted by the employer.

- Site Preparation

The tenderer or the local contractor has to prepare the site. The services will include all deliverables as mentioned below.

The site preparation will include:

Trenching for underground cables, preparation of ways and pipes for wiring are not part of site preparation. The installation contractor has to prepare and use a container as power-house in respect with the individual components manufacturer installation notices if container solution is required

The tenderer will execute the following work in regards to the site set-up:

  - Clearing of scrubs and leveling of grounds

  - Erection of brick buildings to host the batteries, inverters and Generator if required

  - The preparation of an adequate space where the container shall be placed if required

  - Installation of a steel mounting structure on which the panels will be mounted.

  - Storm water drainage works as may be necessary based on the topography of site provided

The installation company is to note that the steel mounting structure will be prepared according to the dimensions of the quoted solar panels. The steel structure will be including the aluminum frames, which are to be supplied by contractor.

- Installation Phase

The installation phase will include the following steps depending on the solar PV hybrid power plant design and specification:

  - Mounting of modules on pre-installed mounting structures

  - Installation of PV grid tied inverters and cabling with the AC distribution

  - Installation of battery inverter charger and cabling with the battery and AC distribution

  - Installation of battery bank and cabling with the system

  - Installation of the Generator and cabling with the system

  - Cabling of solar array, array to grid powerhouse or container

  - Installation of auxiliaries and remote monitoring devices

  - Labeling of the completed system

  - System DC and AC wiring

  - Installation of 0.415/11KV substation and associated protection systems

  - Further necessary installation work

- Commissioning Test

Complete commissioning of the power plant, function tests, and trial service of the power plant. All installations and equipment will be inspected and their functionality will be tested. All components, electrical works and civil works will be visually checked for compliance with the technical specification, Guidelines/Manuals of delivered equipment, build plans, state of the art engineering works.

Commissioning tests will be carried out to demonstrate that the solar PV hybrid power plant is operated according to the technical specifications and under all available operating conditions. The contractor will sign a final acceptance certificate.

The tenderer shall submit with the bid document a schedule of commissioning test to be contacted during testing and commissioning and the expected output values where applicable

- Operator Training

The technical commissioning of the solar plant will include training on the operation of the power plant components. The training will include the maintenance of the batteries, the remote monitoring and operation of the Generator both on manual and automatic mode. It will be verified that the operating personnel are adequately trained.

- Information for Installer Companies

The contractor is obliged to adhere to the Energy (Solar Photovoltaic Systems) Regulations from

2012, which state “A person shall not import, distribute, promote, sell or install any solar PV system unless he is licensed by the Commission as a vendor.

- System Layout

The solar PV hybrid power plant shall consist of following main equipment’s/components following the design specifications of the contractor.

  - Solar module array

  - Mounting structure and civil foundation

  - Hybrid inverters

  - Battery bank

  - Battery mounting rack

  - Diesel generator and diesel tank

  - 415V Control Panel set with 1No incomer and 1 No Feeder panels.

  - 0.415/11KV substation

  - DC and AC-Cabling

  - Control panel with switcher, disconnectors and safety elements

  - Sub-station outdoor equipment – CTs, VTs, Isolators

  - Earthing and lightening protections.

  - Data monitoring system

  - Housing of equipment

12.1 Schematic Diagram

The design of the solar PV hybrid power plant has to follow DC coupled architecture operation. The system has to be modular expandable for future development. The installer has to provide the schematic drawings for approval by the employer before installation.

13. Notice Board

A notice board 1.5m by 1m made of a continuous sheet metal with steel angle line supports 2” by 2” by 3mm and 1.5m high shall be erected at the gate of the beneficiary institutions and shall read as thus:

THIS SOLAR PV HYBRID SYSTEM

AT

(FULL NAME OF THE TRADING CENTRE)

HAS BEEN IMPLEMENTED BY THE NATIONAL GOVERNMENT THROUGH

THE RURAL ELECTRIFICATION AND RENEWABLE ENERGY COPORATION

This writing should cover over 80% space of the notice board (65mm Text Height).

Any other writings should strictly not be included.

      - CIVIL AND STRUCTURAL WORKS

  - Types of works

14.1.1 The civil and structural works to be constructed under this Contract include the following:

-Work for access and SPGP internal road.

-Earthworks for SPGP platform and associated works.

-100mm layer of ballast aggregates to solar field platform.

-Water harvesting and Storage.

-Storm water drainage.

- Perimeter fence, solar field fence substation fence, gate, guard house

-Concrete foundation bases and Mounting works.

-Genset Plinth foundation, its shed and fencing off of the genset.

-Cable trenches.

-Control room containerized technology to accommodate all indoor equipment including BESS.

-Office building containerized technology fitted with furniture (cabinets, chairs and office table) to accommodate two to three operators.

-2 Door VIP Pit latrine.

-Lightning protection system.

- Fire protection system. (Fire extinguishers, fire detection and fire suppression)

-Any other works necessary for full completeness of SPGP.

14.1.2 The contractor shall be responsible for designs of all the civil and structural components and implementation of approved designs. Detailed Geotechnical investigation and Topographical survey at required locations for the purposes of foundation design will be done. The required locations for the geotechnical survey shall be agreed with the employer. The details of beacons and benchmarks shall be provided in the topographical drawings.

  - Control Room

- The control room shall be Containerized Solution. The containers to be made of corrugated steel mounted on reinforced concrete strip foundations raised to allow for self-drainage subject to employer’s approval. The flooring to be made of either chequered plate steel covered with pvc or wood. Metalwork shall be carried out in accordance with the provision of B.S. 5950 and other relevant BS standards. The size of the control room to be a minimum 40 feet container with a minimum height of 9 feet and a standard width of 8 feet cladded with waterproof gypsum. There shall be 2 No. equipment containers with a separate container to accommodate the BESS system and the other container to accommodate other equipment subject to employer’s approval. The wall mounted equipment shall be erected on Medium Density Fireboard (MDF) mounting boards, fixed to design and subject to approval. A separate key board shall be provided for hanging of equipment keys. Adequate cable conduits rails shall be mounted to design and approval for cabling purposes with all trays and fittings provided with a separation between the control and power cables. Cladding of the ceiling and the wall shall be done with materials suitable for insulation and control of temperatures and subject to employer’s approval and painted with three coats of silk vinyl emulsion paint to improve on the aesthetics appearance. The external wall shall be painted with the first coat of red Oxide primer and then consequently painted with Zinc Chromate, anti-rust primer to approved layers and the final coat of paint shall be in accordance to the employer’s approved company color codes. A roof shall be constructed above the container, to allow for heat insulations as well as provide a catchment surface for water harvesting.

- The Control room shall accommodate the following:

        - The Battery Energy Storage System (BESS)

        - The inverters.

        - AC/DC distribution Boards.

        - Remote/local monitoring equipment.

        - All other indoor electrical equipment/switchgear

- The control room shall be fitted with Fire extinguishers to be mounted both indoor and Outdoor on positions approved by the employer.

- The control room shall be fitted with Air Conditioners as specified in this document. The sizes of all ACs shall be optimized design based on the room spaces, temperature and equipment type (including Lithium Ion batteries as per manufacturer’s specifications) and subject to employer’s approval.

- An emergency door exit to be provided in the control room, subject to approval by the employer. Note:The control room design shall be subject to employer’s approval.

  - Office Building.

    - The office building shall be Containerized Solution. The containers to be made of corrugated steel mounted on reinforced concrete foundations raised to allow for self-drainage and to employer’s approval. The flooring to be made of tiles to project manager’s approval. Metalwork shall be carried out in accordance with the provision of B.S. 5950 and other relevant BS standards. The size of the control room to be a minimum 20 feet container with a minimum height of 9 feet and a standard width of 8 feet. The container walls and ceiling shall be cladded internally with material suitable for control of temperatures and subject to employer’s approval and painted with three coats of silk vinyl emulsion paint to improve on the aesthetics appearance. The external wall shall be painted with the first coat of red Oxide primer and then consequently painted with Zinc Chromate, anti-rust primer to approved layers and the final coat of paint shall be in accordance to the employer’s approved company color codes. A roof shall be constructed above the container, to allow for heat insulations as well as provide a catchment surface for water harvesting.

    - Office furniture (cabinets, chairs and office table) to employer’s approval shall be supplied and fixed to accommodate a minimum of three operators.

    - Fire extinguishers shall be mounted on positions approved by the employer.

    - Sufficient windows and ventilation to be provided for lighting and cooling taking into account the expected high temperatures in the proposed project areas.

  - Guard House

- A guard house located at the main gate shall be constructed. The guard house shall be of Masonry. The guard house design shall be subject to employer’s approval.

  - Pit Latrine

14.5.1 A twin VIP masonry pit latrine to design, shall be constructed. The walling and floor to be tiled and doors to be made of steel. A ventilation pipe of minimum 150mm to be installed and the roof sheeting shall be hot dip galvanized troughed mild steel sheeting and shall be of minimum thickness

0.5 mm. A security light shall be provided for purpose of lighting at night.

  - Sequence of Construction

    - The Contractor must complete all the civil and structural works in time to provide a clean and complete site for the mechanical and electrical erection.

    - The Contractor shall be responsible for timely delivery of materials to site and for compliance with the specified or agreed construction program.

    - The office building, control room, guard house and pit latrine shall be constructed away from the solar field to avoid shading effect.

  - Drawings

14.7.1 Any Drawings issued with these documents are for tendering purposes only. Drawings for this project hall be made by the Contractor or his civil consultant, and shall be to the approval of the Employer.

  - Plan of Operations and Temporary Works

    - The Contractor shall, submit to the Employer a fully detailed program showing the order of procedure and method by which he proposes to carry out the construction and completion of the Civil Engineering works, and particulars of the organization and staff proposed to direct and administer the performance of the Works.

    - The information to be supplied to the Employer shall include Drawings showing the general arrangements of his temporary offices, camps, storage sheds, buildings and access roads, and details of Constructional Plant and Temporary Works proposed.

  - Water Supplies, Storage and Reticulation

    - The Contractor shall make his own arrangements for the supply of palatable water for his staff on site and water for construction works and all the mini-grids water needs for the O&M period including soft water for regular cleaning of solar panels as per specifications.

    - The Contractor shall obtain the Employer's or the Project Manager’s prior approval before utilizing any water source for the Works.

    - The quality of water shall be safe for drinking and washing of panels, and should be tested to meet the requirements. Important to Note is that, washing of solar panels does not require salty water and also the quality of drinking water should be within acceptable standards as guided by relevant authorities, otherwise it should be treated and purified if it does not meet the threshold. Storage tanks and distribution tank shall be provided, with one 10,000 liters water tank and one 5000 liters water tank for water harvesting, both ground mounted to supply water in the mini-grids.

    - The cleaning of the panels shall be done using soft water or any other suitable alternative method subject to employers’ approval.

    - The Contractor must make all arrangements to abstract water and must pay royalty to the owners. These costs shall be included in his prices.

  - Employer's Approval of Finished Works

14.10.1 The Contractor shall obtain the approval of the Employer for each section and each stage of

construction. The Contractor shall not proceed with any subsequent stage, until all tests required by the Employer have been carried out, and the results have shown that the section complies with the Specification. Any works rejected by the Employer as not complying with the Specification and quality standards, shall be replaced by the Contractor at his own expense.

  - Basic Survey and Setting Out

    - The Contractor will survey the sites in detail, and the exact locations shall be agreed with the Employer.

    - The details of beacons and benchmarks shall be provided in the topographical drawing.

    - The Works shall be located on the drawings and the Contractor shall appoint a suitably qualified Surveyor to set out the Works from the beacons and shall plot cross sections at 20 m intervals and submit to the Employer for approval.

    - No separate payment will be made for any work in connection with the setting out of the Works, nor any other Works required by the Contractor to ensure the accurate location and construction of the Works.

  - Earthworks

    - Earthworks shall be under the contractors’ scope and considered fully priced by the contractor. The turnkey contractor is responsible for making the site ready by clearing of bushes, removal of trees (if required), leveling of ground (wherever required) etc. for commencing the SPGP.

    - The contractor is also responsible for any necessary earthworks (cut and fill) to modify the site to suitable profiles. Slope protection and landscaping shall also be carried out on any areas with steep Cuts or fills.

    - All earthworks up to formation shall be formed and completed to the correct lines, slopes, widths and levels shown on the Drawings and with the sub grade parallel to and at the correct depth below the profile, camber, cross fall or super elevation shown for the finished level, unless otherwise directed by the Employer.

    - Embankments and fills shall be constructed only of suitable material obtained from the excavation of cuttings. If the Contractor encounters material which he considers unsuitable for earthworks, then he shall forthwith inform the Employer, who shall instruct the method of use or disposal of such material. If insufficient material can be obtained from the cuttings, additional material may be borrowed from approved borrow pits.

    - The Employer may direct that certain soils be excluded from certain layers and other soils set apart or obtained from borrow and used only for these layers, in which case the Contractor shall comply with the Employer's or the Employer's directions and shall allow in his price for such selection of materials.

    - Where, in the opinion of the Employer, unsuitable material occurs in cuttings, the Contractor shall excavate it to the depths and widths specified in the Geotechnical report and replace it with selected fill material to form an improved formation.

  - Order of Work

    - The construction of cuttings, side drains and embankments shall proceed in a methodical and orderly manner. It shall be solely the Contractor's responsibility to arrange his methods and program of work so as to ensure that the earthworks are carried out by the most efficient and economical method possible with the type of plant employed on the Works.

    - All trimming of cuttings and embankments, drains and shoulders to the specified slopes and shapes, shall be carried out concurrently with the earthworks that are being carried out at that particular site and level.

  - Fill Material

    - "Fill-material" shall mean material deposited in accordance with these specifications from any of the classes specified in order to build up an earthworks construction to formation level as shown on the Drawings or as ordered by the Employer. The Contractor shall obtain the fill material from a source approved by the Employer.

    - After doing the necessary earthworks (cut and fill) to modify the SPGP site to suitable approved design profiles, the contractor shall fill the finished ground level (FGL) of the solar field with Murram and compact to the designed FGL formation. In addition to the murram layer at the solar field, a ballast surfacing of minimum thickness of 100mm will be done.

    - Fill materials will generally be obtained from cuttings. If the material obtained from this source is insufficient or unsuitable, extra material shall be obtained from borrow areas. All fill material (other than rock fill in lower layers) shall pass 75mm BS sieve size. The aggregates for the solar field ballast surfacing will be obtained from the nearest quarry, subject to employer’s approval.

    - The following materials are generally unsuitable for construction of fills.

      - All materials containing more than 5% by weight of organic matter (such as top soil, materials from swamps, plants and vegetable matter)

      - All expansive soils such as black cotton soils with swells of more than 3% as measured in the CBR test.

      - All clay soils with plasticity index exceeding 50.

      - All materials having a moisture content of 105% of the optimum moisture content (standard compaction)

    - Rock fill can be used provided that boulders greater than 0.2 M3 in volume or 600 mm in size are not used and that this material is not placed within the top 600 mm to formation level. The best materials from cuttings or borrow areas should be reserved for the upper layers of the fill.

  - Compaction of fill

    - Embankments and fills shall be laid out and compacted to achieve a stable platform with sufficient bearing capacity and stability.

    - Materials other than rock fill shall be placed in layers of compacted thickness not exceeding 300 mm. Thicker layers can only be permitted where very heavy compacting equipment is available and trial sections have proved that the required compaction will be readily achieved over the layer depth. The minimum layer thickness shall be twice the maximum particle size of the compacted material.

    - Fill material shall be compacted throughout to a dry density of at least 95% MDD at OMC (standard Compaction AASHTOT99) except the top 300 mm of the fill which shall be compacted to 100% MDD (AASHTO T99).

    - Where rock fill is used it should be placed in the bottom of the embankment. The largest sizes shall be placed in layers of 1.0 meter thick. The interstices shall then be filled with smaller rocks and approved filler material. The whole layer shall then be compacted until the interstices are completely filled or until the required settlement is obtained. Heavy vibratory rollers are generally the most suitable machines for compacting rock fill.

    - The specified compaction shall be achieved over the full width of the embankment.

Any area inaccessible to the roller shall be consolidated and compacted using approved mechanical tampers.

  - Compaction of in situ Sub grades

14.16.1 After removing the top soil and/or 600 mm of unsuitable /expansive soils or as directed in the geotechnical report and before placing fill, improved sub grade or gravel wearing course, the upper 300 mm of in situ sub grade will be compacted to 100% MDD standard compaction. Compaction in cuts without improved sub grade will likewise be compacted to 100% MDD standard compaction.

  - Spoil Material

14.17.1 "Spoil-material" shall mean material excavated in accordance with these specifications from any of the classes specified, and which, being obtained from the excavation of side drains, cuttings or below the road, embankment is unsuitable for the requirements of the Works. Spoil material shall be removed from the Site to a spoil tip which should be to an approved site acceptable by respective

local authorities and shall be approved by the Employer.

  - Expansive Material

14.18.1 When expansive material is encountered, it shall be removed to a depth 600 mm below the formation or the existing ground level, whichever is greater. Material removed shall be stockpiled for later use in slope protection or spoiled to a tip as instructed by the Employer.

  - Surplus Material

14.19.1 "Surplus-material" shall mean material excavated in accordance with these specifications from any of the classes specified and which is temporarily surplus to the fill requirements and shall be carted to a designated stockpile for re-use later elsewhere in the Works, or to an approved spoil tip.

  - Excavation in "Rock"

    - Excavation Level

Unless otherwise directed, the formation of the platform can be founded on rock. However, rock shall be excavated to an average level 150 mm below the formation and in no place less than 100 mm below the formation.

    - Backfilling for Surfaces

Any excess excavation in rock below the formation shall be backfilled and compacted. Excess excavation in the invert of drains shall not be backfilled, but the rock surfaces shall be trimmed, and all loose particles removed, to allow free drainage of water.

    - Excess Excavation of Slopes

Where side slopes are over-excavated, no backfilling will be required but the slopes shall be trimmed to a neat shape and safe angle as is acceptable to the Employer. The sloping sides of all cuttings shall be cleared of all rock fragments, which move when prized with a crowbar.

    - Hard Material

The provisions of this Clause do not apply to hard and common materials, which materials shall be excavated to the lines and levels shown on the Drawings or as instructed, within the permitted tolerances.

  - Drainage of Earthworks

    - All cuttings, embankments and borrow pits shall be kept free of standing water and drained during the whole of the construction.

    - Should water accumulate on any part of the earthworks, either during construction or after construction, until the end of the maintenance period, giving rise to soaking or eroding conditions in the earthworks, the Employer may order the Contractor to remove and replace at the Contractor's expense any material which has been so affected.

    - All drains shall be maintained throughout the Contract in proper working order.

    - The Contractor must allow in his price for draining the earthworks satisfactorily at all stages during the construction and arrange his methods and order of working accordingly.

    - The entire platform shall be adequately drained and all buildings; control room and office should be well drained.

  - Removal of Top Soil

    - The top soil within the areas of the development of SPGP shall be stripped to an approximate depth of 200 mm and stockpiled at locations agreed with the Employer for later use on embankment slopes or dumbed in approved areas.

    - Overburden in the borrow pit shall also be stripped to a depth specified by the Employer and stockpiled for later use in rehabilitation.

  - Access and Internal Road

    - Suitable approach road and internal access road in all mini-grids within the complex boundary of SPGP as per approved design shall be made to ensure safe and easy transportation of equipment and material.

    - Where necessary access roads to the SPGP sites shall be constructed to gravelling / Murram standard. In general, for gravel access, gravel wearing course materials should comply with the following:

      - They should have sufficient cohesion to bind the particles together and prevent the surface from raveling and becoming corrugated in the dry season.

      - The amount of fines and plasticity should be limited so as to avoid the occurrence of dusty and slippery conditions during the dry and wet weather respectively.

    - Gravel materials are excessively coarse in their “as dug” state. Appropriate processing is therefore necessary to bring them to the required gradation. This is normally done on the road by using grid, cleat or sheep’s foot rollers. Oversized particles which cannot be broken down to the required size shall be removed.

    - The minimum thickness of a compacted layer shall not be less than 125 mm.

    - Internal SPGP road and walk paths shall be compacted to 100% MDD after grading. The road shall have a well-done gravel finish. The road shall be constructed to a fall that will allow proper drainage of the road. The road shall have adequate drainage provided. The design shall be to road design manuals. The road shall have minimum width of Four (4) meters.

    - For the gravel finish internal SPGP road, the single gravel layer should consist of a minimum thickness necessary to avoid excessive compressive strain in the sub grade and to compensate for the expected gravel loss under traffic during the period between re-gravelling.

    - Where the top 300 mm layer of the formation level embankment or natural ground sub grade has a CBR greater than 5%, the following thicknesses shall be provided:

      - Roads not subjected to heavy commercial vehicles– The minimum compacted thickness of 125mm.

      - Access roads outside the SPGP plant and roads within the site likely to be subjected to heavy commercial vehicles during construction and during periodic maintenance. – Provide a 250 mm thick compacted layer.

In addition to the above, where the in-situ sub grade or the embankment material has CBR strength of less than 5% then:

      - Top 300 mm layer of the fill / embankment shall be made with selected imported material with CBR (after 4 days soak) of between 7 and 13%.

      - Where in situ sub grade, an improved sub grade 300 mm thick of imported materials with CBR (4 days Soak) of between 7 and 13% shall be laid.

The above thickness shall extend to cover the shoulders. A cross fall of 4% shall be provided.

    - Compaction will be in layers not thicker than 200 mm and will achieve compacted densities of 95% MDD (Modified AASHTO T180) at compaction moisture contents of between 80% and 105% OMC.

  - Grading Requirements

    - Grading curve of the gravel should be within the class 1 envelope (initial daily number of commercial vehicles less than 150) to guarantee good stability. The grading to consider is that obtained after processing and compaction.

# Table 14.24.2: Gravel Grading Requirements

| Grading after compaction |  |  |
| --- | --- | --- |
| Sieve Size (mm) | % Passing by weight |  |
|  | Class 1 | Class 2 |
| 37.5 | - | 100 |
| 28 | 100 | 95 – 100 |
| 20 | 95 – 100 | 85 – 100 |
| 14 | 80 – 100 | 65 – 100 |
| 10 | 65 – 100 | 55 – 100 |
| 5 | 45 – 85 | 35 – 92 |
| 2 | 30 – 68 | 23 – 77 |
| 1 | 25 – 56 | 18 – 62 |
| 0.425 | 18 – 44 | 14 - 50 |
| 0.075 | 12 – 32 | 10 - 50 |

  - Plasticity Requirements

14.25.1 Plasticity index of the gravel should not exceed 15 and shall not be less than 5 in wet areas (annual rainfall greater than 500 mm per year). In dry areas (annual rainfall less than 500 mm per year) maximum plasticity index shall be 30 but subject to a minimum of 10.

  - Bearing Strength Requirements

14.26.1 A minimum CBR (after 4 days soak) of 20% at 95% MDD and OMC (Modified AASTO T180) is required.

  - Quality Control

    - Tests shall be performed by the contractor on soils and gravels undergoing compaction under the supervision of and at frequencies determined by the Employer and shall include:

      - Determination of the Atterberg Limits in accordance with BS 1377.

      - Determination of particle size distribution in accordance with BS 1377.

      - Determination of dry density / moisture content relationship in accordance with BS standard compaction and modified AASHTO T180 as appropriate.

      - California Bearing ratio (CBR) in accordance with AASHTO T193.

      - Field dry density as set out in BS 1377.

  - Tolerances

14.28.1 The following tolerances will be permitted in the finish of the formation to roads and platform:

- The level of the formation should be within +/- 100 mm of that specified.

- On the final trimmed slope of earthworks, a variation of + or - one fifth of the specified slope will be allowed.

- The tolerances permitted in the overall width of the bottom of cuttings shall be plus or minus 150 mm in the distance between center lines and the toe of cuttings slopes, and plus 150 mm in the case of embankments.

  - Materials for The Works

    - General

      - All materials shall comply with appropriate local or regional standards unless otherwise required hereinafter. Such standards shall be to the approval of the Employer.

      - The Contractor shall before placing any order for materials or manufactured articles for incorporation in the Civil and structural Works, submit for the approval of the Employer the names of the firms from whom he proposes to obtain such materials, etc., together with a list of the materials and manufactured articles giving the origin, quality, weight, strength, description, etc., which he proposes that the firms should supply. No materials or manufactured articles shall be ordered or obtained from any firm of which the Employer shall not have previously approved.

      - All materials shall be delivered to the site within sufficient period of time before they are required for use in the Works to enable the Employer to take such samples as he may wish for testing and approval. Any materials condemned as unsuitable for Works shall be removed from the Site at the Contractor's expense. Contractors price to include these testing of materials.

      - The Contractor may propose alternative materials to those specified, provided that they are of equivalent quality and, subject to the Employer's or the Employer's approval such materials may be used in the Works.

    - Standards

Concrete pipes, porous concrete pipes, cast iron manhole covers and gratings, bricks, concrete kerbs, bituminous surfacing, cement, steel and aggregates shall comply with local or regional standards as per specified standards in the document.

    - Stone for Pitching

Stone for pitching to drains, inlets and outlets of culverts, to embankments and around structures shall consist of sound un-decomposed rock. Precast concrete tiles may also be used.

    - Stone for Solar Field Platform Surfacing

- The stone shall be hard and durable crushed rock with a maximum particle size of 60 mm and not more than 15% shall pass a 9.5 mm sieve.

- The stone layer to be spread uniformly over the finished surface of the platform shall have a thickness of 100 mm.

  - Drainage and Storm Water

    - The contractor shall construct the SPGP station to a fall that will allow proper self-drainage of the site. This shall be done in conjunction with the earthworks design to ensure no flooding shall be experienced within the site. The drainage designs shall refer to data acquired from the Kenya

Meteorological department with site specific criteria over a period of minimum 50 years and shall provide for the worst-case scenarios. The number of runs and outfalls and pipe sizing must be sufficient to cope with the severest precipitation, with a factor of safety of 1:2 within the SPGP site and other areas in the site. The drainage must allow uninterrupted access.

    - Drainage shall be in accordance with relevant Codes for Practice published by authoritative Standards organization such as the British Institution, e.g., BS 8301, BS 6031 and Eurocodes.

    - Embankments and cuttings are to have drainage facilities at their top or bottom. The formation level of the site is to be formed with uniform cross-falls of about 1 in 300 in the same direction as the natural drainage path of the surrounding environment. Drainage minimum slope shall be 1 in 200.

    - Surface water from roofs of buildings shall be drained to down pipes, which connect with the general site drainage system. Surface water from the control room building and office roof shall be drained to the main storage reservoir tank.

    - In areas where there is a risk of water runoff the SPGP Plant shall be protected from failure by means of gabions, retaining walls, and stone pitching or otherwise to the employer’s approval.

  - Boundary Fencing and Additional Security Measures

    - Fencing

The contractor shall fence the entire perimeter of the acquired land, to secure the developed area (Solar Field, Office, Control room etc.). There shall be a second fence to barricade the solar field, located at a sufficient distance from the solar panels, to avoid shading effect. The third fece shall be for the substation area. The Contractor shall construct all the three fences including gates where necessary and shall comply with the requirements of the following Clauses. The design of the fences shall be subject to employer’s approval.

- All the perimeter fences shall be of chain link with concrete posts. The fencing shall have barbed wire on top of the perimeter fence. Perimeter lighting shall be provided to employer’s approval.

- The Solar Field fence shall be of chain Link with steel sections of optimized design, with a minimum height of 1.5m, to barricade unauthorized persons from accessing the Solar plant area.

- Dimensions

Height of chain link fabric for the perimeter fence:	2 400 mm Height of chain link fabric for the Solar Field:	1500 mm

    - Barbed wire: 3 wires above fabric, height of 300 mm, on supporting arms facing outwards from Site at 450 angles.

Maximum distance between posts or columns: 3 000 mm, except where interrupted by gate.

    - Tension bars and bands: located at terminal posts to fix fabric, bottom wire and barbed wire.

    - Top rail: "extra-strong" pipe, 43 mm outside diameter.

    - Braces: "extra-strong" pipe, 43 mm outside diameter for attaching end and gate posts to adjoining posts. Use two braces at corner and restraining posts.

    - Gate width: free distance between 2 gate posts, 1 500 mm for single gate, 5 000 mm double gates.

    - Double gates: one leaf for normal traffic, other leaf to remain closed by means of drop bolt locking into center rest, inoperable from exterior.

    - Gates: able to open in either direction to 900.

    - Gate hardware: three hinges, latch with padlock accessible from either side of gate, latch catch.

    - Top of posts and uprights: weatherproof tops.

    - Materials

      - Fabric: ASTM A 392, 2 000 mm high, 3.8 mm diameter (No. 9 gauge) steel wire, 50 mm diamond pattern, twisted and barbed finish at top, knuckled wires at bottom, zinc coated.

      - Pipes: ASTM A 120, steel pile, hot-dipped zinc coated after welding, diameter and weight size as shown on drawings, unthreaded ends, free from burrs.

      - Fence fittings: ASTM F 626, hot-dipped zinc coated according to ASTM A 123.

      - Barbed wire: ASTM A 121, 2.51 mm diameter wire in strand (No.12-1/2 gauge), 3 strands with 4-point barbs spaced at 125 mm, Class 3 zinc coating.

      - Bottom wires: 5 mm (No. 6 gauge) steel wire, 500 g/m2 zinc coating. This shall be surrounded by a concrete beam (C20), to hold down the fabric.

      - Fence fittings: ASTM F 626, steel tension bars and bands, nuts and bolts, weather proof tops of commercial aluminium alloy, malleable cast iron, or rolled or pressed steel, cast iron and steel fittings hot-dipped galvanized with 500 g/m2 according to ASTM A123.

      - Concrete: 20MPA at 28 days

    - Installation

- Install fencing and gates according to ASTM F 567 unless otherwise indicated, and to drawings and this Specification.

- Level ground surface so that space between finished ground surface elevation and bottom of fabric does not exceed 50 mm.

- Plumb and align posts to within 10 mm.

- Install posts of the gate at same elevation regardless of difference in ground level.

- Set posts in concrete footings in form of truncated cone, according to ASTM F 567, and as follows:

# Table 14.31.5.1: Chain Link Concrete Post Footings Guidelines.

| FOUNDATIONS (Dimensions) | ORDINARY SOIL |  | SOLID ROCK |  |
| --- | --- | --- | --- | --- |
|  | Line Posts | Terminal Posts | Line Posts | Terminal Posts |
| Depth Diameter at top Diameter at bottom | 1000 mm 250 mm 350 mm | 1600 mm 300 mm 400 mm | 300 mm 150 mm 150 mm | 500 mm 150 mm 150 mm |

Make joints in fabric at terminal posts.

- Fasten as follows:

        - Every 450 mm along top rail, braces and bottom wire;

        - Every 300 mm on line posts.

Secure barbed wire to terminal and gate posts with tension bands, and to gate uprights with hooks.

- Install bottom wire in middle of last line of mesh.

  - Additional Security Measures

The contractor shall provide the following additional security measurers;

    - Warning plates/danger plates etc. shall be provided in sufficient numbers all around the fencing as per safety requirements.

  - Concrete Works

    - Soil Investigations

The contractor shall collect all data he deems necessary for preparation of his bid. The foundation design shall be based on the bearing strength data, obtained from the geotechnical survey.

The Contractor shall be required to perform sub-soil tests within the area of the SPGP to the depth and by the method of test specified by the Employer. The details of performing the test, tools and equipment to be used for, shall be submitted to the Employer for approval.

The sub-soil tests shall be carried out by any method as stated hereafter under the supervision of a qualified person, who shall be subject to approval of the Employer.

    - Excavation

Excavation for concrete foundations shall be carried out in strict accordance with the requirements of the Employer and to fit in with the program of construction.

    - Shoring and Timbering of Excavation

The Contractor shall be entirely responsible for the safety of all excavations, for the prevention of injury to workmen and for the stability of the faces of the excavation.

The adjacent road surfaces must remain trafficable, and cracking or cave-ins must be avoided. All shoring and timbering shall be done to the approval of the Employer, who may order such shoring or timbering to be strengthened or altered if he considers this necessary in the interests of the work or to safeguard against accidents to workmen or cave-ins. For the purpose of measurement, the following categories of shoring shall apply:

    - Dewatering

The whole Works shall be constructed in dry conditions and the Contractor shall be held responsible for keeping all excavations free from water, whatever the source or cause may be, and shall properly deal with and dispose of water by use of sufficient temporary works, plant and appliances so as to ensure that the whole Works is executed in a satisfactory dry and safe manner, and costs for all dewatering operations shall be included in the price for civil works.

    - Excavation to be approved

In no case shall broke stone for under drainage or concrete be placed in an excavation until the surface on which such materials are to be placed has been approved by the Employer.

The Contractor shall advise the Employer whenever the bottom of any excavation is ready for inspection or whenever it is necessary to cover up the work. In default of such notice the foundation shall on the order of the Employer be uncovered by the Contractor and reinstated without extra charge.

    - Disposal of Excavated Material

All material excavated under this Contract shall be disposed of in accordance with the instructions

issued by the Employer. Selected material required for back-filling shall be removed to a tip found by the Contractor and the Contractor shall be responsible for ensuring that the required amount of spoil is set aside.

    - Other Services

Where trenches pass near or across other services, the Contractor shall take every precaution against damaging such services. These services shall be properly supported in the trench until back-filling is complete and the back-filling shall be thoroughly compacted under and around such services.

    - Backfilling

Back-filling shall be carried out either with selected spoil as set aside, or with imported selected spoil, or other material to the approval of the Employer. No back-filling shall be done until all the formwork has been removed together with pieces of timber, cement bags, vegetation and or other rubbish.

All back-filling shall be compacted in layers not exceeding 150 mm thick and shall be sprayed with water to bring the moisture content to the optimum for dense compaction.

Compaction shall be to approved standard.

  - Concrete, Formwork and Reinforcement

    - Material

      - Aggregates

- Shall conform to BS 882.

- Shall be heaped separately on hard, self-draining surfaces.

- Normal size of coarse aggregate shall be 20 mm.

      - Water Shall be fit to drink

      - Reinforcement Shall conform to BS 4449.

      - Reinforced Concrete

Shall be designed to BS 8110, Foundation BS 8004

      - Steel

Shall be designed to BS 5950

      - Cement Shall

- Conform to BS 12.

- Be either normal Portland or P.C. 15.

- Be used within 6 weeks of manufacture.

- Be stored in a manner to exclude any moisture.

- Be stored in a manner to ensure use of the earliest consignment.

- Different types of cement from different manufacturers shall not be mixed for a single cast or structural element.

- Additives shall not be used

    - Before concreting

      - Design Mixes

Not less than 2 weeks before the start of concrete work, the Contractor shall submit to the Employer for his approval a statement of proposed mix proportions for the various grades required in the project. (Note: the grade is the characteristic strength or the cube strength below which not more than 5% of the result may be expected to fall when tested at 28 days).

The statement shall include proportions of cement, fine and coarse aggregate, and water, the maximum and minimum slump and the target strength for each grade.

A certificate by recognized laboratory that the proposed mix will meet the requirements must accompany the statement.

The proportions stated may not later be altered without the written approval of the Employer. Cost of mix designs to be borne by the Contractor.

      - Formwork

Formwork shall be sufficient to leave the concrete finishes specified on drawings and to be within the tolerances specified in the following table and to provide an acceptable surface for applied finished, where required.

Line and Level	1 mm per meter not exceeding 5 mm Pockets, Sleeves etc. +/- 5 mm

Bases	+/- 50 mm

The concrete shall have a smooth finish free of projections, voids, etc. The type of ties to be used shall be such that the required finish is achieved and does not become marred by subsequent corrosion. Ties to be set out to definite pattern to the Employer's or the Employer's approval. Rubbing down is allowed only after the Employer's approval of the surface to be treated.

      - Reinforcement

Shall not be heated or re-bent without the Employer's permission.

Shall be free from any material likely to impair bond or initiate corrosion.

Shall be bent and fixed according to the Employer’s approved bending schedules. Shall be tied with soft iron wire.

Shall be supported to maintain the following minimum cover during concreting.

        - The greater of the diameter of the bar or 40 mm for external un-plastered face.

        - The greater diameter of the bar or 15 mm for internal face. Shall be inspected by the Employer.

      - Construction Joints

Shall be avoided, if possible, but if inevitable shall be pre-planned in consultation with the Employer and temporary stop ends inserted. Before placing of concrete against a construction joint, the formed face shall be hacked down to expose the coarse aggregate, kept continuously wet for 24 hours. Vertical faces should be covered with cement/water slurry and horizontal faces should be covered with 15 mm layer of cement/sand grout. New concrete should then be placed immediately.

      - Camber

To formwork shall not be at the expense of the overall depth of the concrete.

      - Weather

The expected temperatures in Homabay region is more than 30 degrees Celsius. The contractor shall adopt use of membranes for curing, to manage the desired moisture and temperature conditions and hydrate the cement to avoid concrete cracking.

      - Batching Shall

- Be by mass in accurately calibrated scales or be volume in soundly constructed gauge boxes making due allowance for bulking of the fine aggregate.

- Be in proportion to whole sacks of cement.

      - Mixing Shall

- Be in a machine in good condition, large enough to carry the whole mix, controlled by a competent experienced operator.

- Be for sufficient time to ensure complete mixing of the ingredients.

      - Placing Shall

- Be under the control of a competent, experienced overseer.

- Be in a manner to prevent separation of the ingredients.

- Be a continuous process until the pour is complete.

      - Compaction

- Shall be by immersion (poker) vibrator in the hands of experienced operators.

- Concrete shall not be moved by vibrator.

- Shall be sufficient to remove all air pockets and honey-combing and to ensure complete dense concrete cover to all reinforcement.

      - Testing

a) Making of concrete cubes by Contractor under Employer's supervision. Contractor shall arrange for transport of cubes to approved testing laboratories. Cubes to be in sets of 3.

      - Curing

- Shall commence early on the morning following the placing of the concrete.

- Shall be effected by keeping the concrete in a permanently wet state.

- Membranes shall be used due to expected high temperatures.

- Shall continue for a minimum of fourteen (14) days or such longer time as may be required by the Employer.

      - Stripping of Formwork

- To soffits shall not be struck until 7 days after placing of concrete (but see below for (props).

- To vertical faces shall not be struck until 14 days after placing concrete.

- Props to soffits shall not be struck until 14 days after placing concrete.

- Shall not be stripped without the Employer's approval who has the power to vary the above items.

      - Patching

- To defective work shall not be undertaken before the item has been shown to the Employer.

- Is a sign of poor workmanship. The Employer shall have the right to reject the complete element if an unreasonable amount of patching has to be done, or if patching will spoil the appearance of the finished concrete.

14.34.2.16 Records

Are to be kept by the Contractor, showing date and time of each concrete pour, the weather conditions, the temperature, the number of the cubes which represent the concrete, the slump and any other items which the Contractor and/or the Employer consider relevant. These records are to be made available for the Employer’s inspection when required.

  - Foundations

The contractor shall construct reinforced concrete structural foundations for the Equipment Enclosure as well as for the Solar Equipment as required. These shall be designed to relevant standards and reviewed by the Employer before implementation.

  - Cable Ducts and Conduits.

    - The Contractor is responsible for all civil engineering works required for the cable runs between the Solar field site and the control room and/buildings, in buried heavy gauge installation ducts of minimum 150mm to connect cables from the solar panels and equipment to the Control room and/office as required. Manholes for inspections shall be provided at approved intervals.

    - Where the cable trench is crossing roads, the ducts shall be constructed in such way that they will be able to withstand the weight imposed on them.

    - The contractor shall appropriately mark the cable route.

    - Cable entries into buildings/control room and road crossings shall be through 150 mm diameter heavy gauge ducts.

    - Two (2) lines of 150 mm diameter heavy gauge of spare ducts shall be provided.

    - After installation of cables the ducts shall be sealed with duct sealing compound where required. Cable entries into building/control room shall be sealed to prevent the entry of dust, vermin water, etc., using suitable materials

    - The cable system design including manholes shall be subject to employer’s approval.

  - Builder's Work

    - Setting out Walling

The Contractor shall provide proper setting out rods and set out all work on the same for courses, openings, heights, etc. and shall build the walls and piers, etc. to the widths, depths and heights indicated on the drawings and as directed and approved by the Employer.

    - Materials

      - Cement

Cement shall be as described in concrete Works, Part 5.34.1.6

      - Fine Aggregates

Fine aggregates for concrete blocks shall be as described for fine aggregate in Concrete Works.

      - Coarse Aggregate

Coarse aggregate for concrete blocks shall be good, hard, clean aggregates from an approved quarry. It shall be free from all de-composted materials and shall be graded up to 7 mm, and all as described for coarse aggregate, Concrete Works.

      - Machine cut stone.

This shall be to approval of employer and meet minimum required specifications.

      - Concrete Blocks.

Concrete blocks for walling shall be provided by the Contractor complying with B.S. 6073, and made in approved block manufacturing machines.

Minimum thickness of blocks in external walls shall be 150 mm, and in internal walls the thickness shall be minimum 100 mm.

Samples of the proposed block types shall be approved by the Employer before any walling work is commenced.

Blocks shall be cast under sheds in suitable block manufacturing machines either power driven or hand operated. The form shall be of steel, and accurately made to size to give the required shape and squareness of block. The concrete shall be vibrated during casting to achieve a dense and uniform concrete. The material shall contain only sufficient water to obtain full chemical reaction of the cement and to give proper workability of the constituents.

The ratio of combined aggregate to cement shall not exceed 3:1. The Contractor shall present his proposal for mix recipe supported by test results for the Employer's approval.

Concrete shall have minimum 28 days strength of 20 N/mm2 in accordance with B.S. 1881. Mixing shall take place in mechanical mixers so as to thoroughly mix the constituents to a uniform consistency before casting.

On removal from the machine the blocks shall be carefully deposited on edge on boarding or a clean concrete floor under sheds so as to prevent drying out by the sun for 3 days. During this time blocks shall be kept constantly damp. The blocks may then be laid on edge in the open and kept damp by spraying or covering with wet hessian or by other means for a further 5 days. The blocks may then be stacked if required, but not more than one meter high, and in such a way as to prevent damage to the edges and corners.

No blocks may be used in building or be transported to site before having reached required 28 days strength criterion. All concrete blocks shall be of even texture and properly mixed ingredients and all portions of the block shall be properly set and hardened concrete.

Blocks shall be free from cracks or blemishes and shall be true to shape and size with clean sharp edges and corners and with corners truly square. Damaged blocks shall immediately be removed from the site. No dimension of a block shall deviate individually by more than 3 mm from the correct size. The average length, width and height of a sample of 15 blocks should neither be longer nor less than 2 mm than the correct size.

Dressed natural/foundation stone blocks at least 200mm width may be used as alternative to the concrete blocks.

      - Cement Mortar

The cement mortar is to be mixed in the proportions of 1 Cement, 4 Sand, and thoroughly incorporated with a sufficiency of water. Any cement mortar which has been left for more than one hour shall not be used in the Works.

      - Building Walling

All blockwork shall be laid in raking stretcher bond solidly bedded, jointed and flushed up in mortar.

Where wall faces are to be plastered the joints shall be raked out to form a key. The blocks shall be thoroughly wetted for at least 24 hours before laying. Walls shall be carried up evenly course by course. During laying an open joint not less than 15 mm wide shall be left between the ends of all concrete lintels, whether pre-cast or cast in-situ and the blocks adjacent to these ends. These open joints shall be left as long as possible during construction and not filled until plastering or other works render such filling necessary. All such joints shall be properly filled in before the completion of the work. External walls shall be reinforced with two 8 mm high yield steel bars in every third horizontal mortar joint. The building shall be designed as a framed structure.

Blockwork which is not to be rendered or plastered shall be finished with a fair face and the blocks shall be selected for even texture and unmarked faces, regular shape and square unbroken arises. The blockwork shall be pointed as the work proceeds with a neat joint. Where blockwork is to be rendered or plastered the joint shall be raked out 10 mm deep as the work proceeds to form an adequate key. Galvanized steel ties with fishtailed end cast into the concrete spaced at alternate courses and extending not less than 150 mm into the block joints. All mortar joints are not to exceed 15 mm or less than 12 mm.

      - Lintels

Concrete lintels shall be used for all openings and shall be reinforced and constructed as per approved structural designs for the gourd house.

  - Structural Steelworks

    - Structural steelwork shall be shop-fabricated from structural shapes of medium grade carbon steel in suitable lengths for easy transport and erection. The structural members shall be jointed or fixed on site by bolting or welding. Site welds should be minimized. Design shall comply with BS 5950.

    - All workmanship and fabrication shall be in accordance with the best practice and shall generally comply with the requirements of B.S.4449. The greatest accuracy shall be observed to ensure that all parts fit together correctly on erection within the tolerances stated in this section. Steelworks shall include all materials, bolts and attachments, cleats, brackets, gussets, etc.

    - Where required in the Contract, the Contractor shall design the steelwork to comply with the information given on the Contract Drawings. Loading and factors of safety shall comply with relevant codes and regulations. Shop drawings shall be prepared using welding symbols to B.S. 499 where appropriate. Design calculations and shop drawings must be submitted to the Employer for his approval prior to fabrication of members. The approval of shop drawings and calculations by the Employer shall not relieve the Contractor of the full responsibility for any discrepancies, errors,

Omissions or failure arising therefrom.

    - All steelwork shall be transported, handled, stored on Site and erected so that members are not damaged or subjected to excessive stresses. Fabrication and erection shall comply with B.S. 5950 Part 2.

    - The contractor shall provide steel support structures to support all equipment and solar panels at a minimum of 1m clearance from the finished ground level, on the lower side of the elevated panels.

    - The structures shall be galvanized to the required specification, with a minimum coating of 614mg/m2.

    - The Mounting of the Solar panels shall be done on steel rails and frames and shall be designed to carry all the loadings and in accordance to provision of B.S 5950 and any other relevant BSI standards.

  - Roofing-Control Room, Office Building Guard House and VIP Latrine

    - Materials, accessories and fixings shall be ordered from an approved supplier and the Contractor shall as and when required by the Employer, submit and deliver samples of all materials for inspection and testing. Roof trusses shall be in steel.

    - Roof sheeting shall be hot dip galvanized troughed mild steel sheeting and shall be of minimum thickness 0.5 mm. The sheeting shall have approved plastic coating on face side. Type and brand of such sheeting shall be proposed by the Contractor with his Tender together with supporting specifications.

    - The sheets shall be laid with 200 mm end laps and double corrugation side laps away from the prevailing wind. The sheets shall be fixed to light gauge steel purlins with galvanized coach screws and seating washers.

    - Holes for screws shall be carefully drilled in the ridges of the corrugations. Great care shall be exercised to avoid damage and disfiguration to the surface coating of the sheets.

Maximum load acting on the building shall be in accordance with local or regional standards.

  - Roof Drainage

    - Gutters and down pipes shall, unless otherwise shown on the drawings, be approved plastic coated steel or heavy gauge PVC of diameters 200 mm and 150 mm respectively.

    - Joints shall be lapped 150 mm in the direction of the flow and soldered. Slip joints shall be provided to allow for expansion. All hangers, brackets, and fastenings should be of the same metal as the gutter or of compatible materials. Gutters and down pipes including supports shall be designed for a concentrated load of 100 kg. Screens or strainers shall be provided to prevent debris from clogging the down pipes.

  - Metalwork and Containerized Control Room Solutions.

    - Unless otherwise specified, metalwork shall be carried out in accordance with the provision of B.S. 5950 and other relevant BSI standards.

    - All steel shall unless otherwise specified, be hot dip galvanized. The minimum galvanized coating shall be 614mg/m2.

    - For the case of containerized control room, the material shall be in good condition, Durable and environmentally friendly. The containers shall be fitted with insulations for temperature regulations, as an addition to Air conditioners installed for temperature control to specification, due to sensitivity of the equipment to high temperature conditions. Rejected containers due to poor Quality, shall be replaced at the contractor’s expense. The container shall be painted with the first coat of red Oxide primer and then consequently painted with Zinc Chromate, anti-rust primer to approved layers and the final coat of paint shall be in accordance to the employer’s approved company color codes.

    - Prior to fabrication the Contractor shall submit shop drawings for the Employer’s approval.

  - Metal Doors

    - General

Metal doors shall be supplied by approved manufacturers.

All doors shall be painted as specified under Painting and Decorating. All locks shall be master-keyed with three master keys supplied in addition to three regular keys for each door or gate.

Doors shall be measured by the number of doors of specified dimensions. The rate shall include all supplies, site works, painting and hardware.

    - Doors

Door frames shall be pressed steel frames made from minimum 2 mm thick steel sheeting and reinforced where door closers are fixed.

Thresholds shall be made from rolled steel sheeting approximately 100 mm wide and 12 mm high. Placing of doors in accordance with control room and office building drawing.

Internal door frames are to be built to walls truly vertical and square with three ties per frame. External door frames are to be built in to walls truly vertical and square with six ties per frame.

All door frames are to be from an approved manufacturer and illustrated in the Manufacturer's Catalogue.

Door frames are to be complete with 100 mm, loose pin steel hinges welded in position and adjustable striking plate.

Door frames and similar components shall be fixed with countersunk screws or bolts with heads set into the frames.

Doors wider than 800 mm shall have three 100 mm hinges. Other doors may have two hinges except where specified or detailed otherwise.

Door stops shall be fitted by screwed fixings where necessary.

  - Aluminium or Steel Windows

Unless otherwise indicated windows shall consist of aluminum sub frame with clear glass. Windows shall be from an approved supplier and the details thereof shall be approved by the Employer. Windows shall be operable and provided with corrosion resistant metal insect screens or as directed by the Employer.

Frames shall generally be built-in during construction of the walls and securely fixed.

Placing of windows in accordance with approved control room and office building drawings. Windows are to be built in to walls truly vertical square with six ties per frame.

All aluminum or steel windows are to be from an approved manufacturer and illustrated in the Manufacturer's Catalogue.

Windows are to be fitted complete with casement fastening, stays etc.

All windows shall have approved burglar bars, and approved means of opening/locking.

  - Door and Window Furniture

Ironmongery shall be strongly made, well finished and of good quality. Ironmongery for windows and doors shall be galvanized or other approved manufacture for external use. Samples of all items shall be submitted to the Employer for approval before they are used for the Works.

All doors shall be lockable. External doors shall have approved security locks.

Three keys for each lock, clearly labelled, shall be placed in a key cabinet in the control room and all ironmongery shall be cleaned, oiled, adjusted and left in perfect working order.

Emergency doors shall be provided accordingly as per the safety requirements.

  - Control room, Guard House, VIP Latrine and office building

The specifications of the finishing should be read in conjunction to section 5.2 and 5.3 for the containerized control room and office.

# Table 14.45.1: Schedule of Materials and Finish

| ROOM | FLOOR | WALLS | CEILING | REMARKS/NOTES |
| --- | --- | --- | --- | --- |
| Control room/ Office building | Wood tiles/ Ceramic tiles/steel chequered plate | Cladding with Approved material | Cladding with Approved material | Subject to employer’s approval |

NOTES:

Sheets for ceilings: prefabricated/manufactured color and type in according to approval of the employer.

Control room and office building:	External/internal color in accordance with approval of the employer.

      - Plaster and Floor Coverings Materials

Cement and water to be as before described. The sand to be screened through a sieve of 10 to 15 and meshes to 1 cm and to be washed if directed.

    - Mixing

All materials for mixing are to be used in proper gauge boxes and they are to be strike measured and not tamped down in boxes. Proper non-absorbent stages are to be used for mixing and storing mortar. No foreign matter must be mixed with the mortar.

The materials are to be mixed dry before adding water through a fine hose spray. No cement mortar which has taken its initial set will be allowed to be used.

    - Plaster Thickness

Unless otherwise specified all wall plasters should not be less than 13 mm thick and not more than 19 mm thick.

    - Cement Plaster

Cement plaster for external use to be composed of one part cement to four parts sand and for internal use to be one part cement to five parts sand.

    - Form Key

Rake out joints and roughen if necessary to form key for plaster.

For concrete surfaces, hack and apply 1:1 cement sand slush to form key. Continuously wet for 7 days and then apply plaster.

All brickwork and concrete works should be brushed down to remove dust and any other loose material.

    - Wetting

All internal and external brick or concrete surfaces are to be wetted well before plastering. All cement plaster must be kept wet for at least 7 days.

    - Repairing Defects

All defective plaster, cracks, hollows, etc., are to be cut out to a rectangular shape, the edges undercut to form a dovetail key and to be made good to finish flush with the edge of the surrounding

Plaster work.

All patches will be to the approval of the Employer and if the defects cannot be made good satisfactorily then the whole surface is to be removed and re-plastered at the Contractor's expense.

    - Glazing and Painting

      - Glass

All glass is to be of approved manufacture, free from bubbles, waveness, scratches or other imperfections and is to be well bedded, puttied and back puttied and secured with glazing pins or clips in steel sashes or with sprigs in wood sashes.

All glass shall be carefully cut to the required sizes so that all panes of figured or textured glass are uniform in appearance with the pattern parallel to the edges and wired glass shall be so cut that the wires are parallel to the edges.

The window glass for control room shall be shatterproof type.

      - Putty

Putty for glazing to steel sashes is to be of approved proprietary brand. Rebates are to be thoroughly back puttied before glazing and all putty is to be carefully trimmed and cleaned off so that back putty finishes level with the top of sections internally, external putty covers sight lines exactly and finished straight and true. Rough surfaces to putty will not be allowed and any defective putty will be cut out and replaced at the Contractor's expense.

Rebates of wood sashes are to be given one coat of priming immediately before glazing.

      - Mirrors

Glass mirrors are to be of the thickness specified, of selected quality glass, silvered on back, with protective sealing coat and arrised edges, unless otherwise described.

Generally

Allow for removing and replacing all cracked, broken or defective glass and leave thoroughly clean and perfect at completion.

    - Materials for Decoration

All paints, primers, varnishes, emulsions, stopping, etc., to be of approved manufacture. The contractor is to use proprietary ready mixed paints obtained from an approved supplier.

When a coat of proprietary paint is applied, the manufacturer's priming and previous coats suitable for the particular type are to be used.

All materials must be brought on to the site in unopened tins, and no dilution or adulteration will be permitted, unless approved by the Employer.

    - Emulsion Paint

Emulsion paint shall be PVA (Polyvinyl Acetate) alkali-resisting formulated with high washability

and capable of resisting a 8000 scrub test. The first coat to be specially formulated base coat for direct application to the specified surface.

    - Fillers

Higher grade cellulose fillers are to be used internally and premixed filler to be used externally.

    - High Gloss Paints

Primers for application to bare metal to be red oxide primer for iron and steel. For galvanized metal to be an approved zinc chromate or galvanized iron primer. For application on wood or plaster etc., to be an approved alkali primer.

    - Finish enamels

Finish enamels to be synthetic enamel high-capacity paint with high coverage and high gloss finish unless otherwise described.

    - Workmanship

All surfaces are to be free from moisture, dust, grease and dirt and rubbed down smooth according to approved practice.

All plaster to be free from efflorescence and treated with one coat of petrifying liquid, approved sealer or alkali primer if required. Hard wall plaster to be glass papered before decorating.

Rectifying defects to decorated surfaces due to dampness, efflorescence, chemical reaction, etc., will be to the Contractor's account, as these surfaces must be checked and the appropriate precautions taken before applying the decoration.

Metalwork must be scraped free of rust, primed as described and finished as later specified. Galvanized sheet iron, pipes, etc., are to be cleaned down to remove manufacturer's ammoniated dichromate protective covering, primed as described and finished as later specified.

Coated pipes are to be cleaned down, stopped and primed with one coat of aluminum primer and finished as later specified.

All metal to have the specified number of coats in addition to the priming coat.

Every coat of paint must be a good covering coat and must dry hard and be well rubbed down to a smooth surface before the next coat is applied, otherwise the Contractor will be required to apply extra coats at his own expense.

Each coat of paint to be of a distinctive color: sample colors are to be prepared for the final coat which is to be an approved color scheme and must not be applied without the permission of the Employer. After undercoats are on, the painter shall check all work and grain fill as necessary with filler as described.

NOTE:

- All paints specified are to be obtained from an approved manufacturer and used in strict accordance

with their instructions. Their representative will check the paints being used and the method of application and will advise accordingly.

- This section of the work to be carried out by an approved firm of decorators who must allow for the very best finish possible and of the highest quality obtainable.

- The prices must allow for the removal and refitting of all beads, fittings, fastenings, ironmongery, etc., removed for decoration purposes to be carried out by skilled tradesmen of the appropriate trade.

  - Control Room and Office Building Sizes.

The sizes are as specified in clause 5.2 and 5.3 of this document.

  - Ironmongery and Metalwork

    - General

All ironmongery shall be of the best respective types required and no alternative articles will be accepted unless approved. Articles described as brass must be solid brass and not brass finish. Chromium plated articles must be plated satin finish on solid brass or other approved metal.

Where items for ironmongery are required to be fitted to steel door frames, etc., the Contractor must ensure that the Manufacture makes provisions for the correct fitting or lock striking plates, hinges, cleat holes, bolt keeps, etc.

    - Locks and Keys

Locks are to be two levers unless otherwise described. All locks are to be provided with two keys which must be handed over to the owner on completion of the Works with identification labels attached.

    - Steel

Steelwork for general building construction is to be of approved manufacture complying generally with the appropriate British Standards and free from all defects, oil, dirt, loose rust, scale or other deleterious matter.

  - Electrical Installation

    - The contractor shall supply, install, test and commission the complete electrical services within the Control room both outdoor and indoor, office building both outdoor and indoor, Guard house, VIP latrine and SPGP outdoor security lighting/perimeter lighting.

    - The complete electrical installation shall comply with all local standards and rates and shall be as per KPLC requirements/specifications.

    - Lighting

- Luminaries shall be fluorescent lamps except for the toilets and outdoor lighting. SPGP and/Perimeter Outdoor lighting to use flood lights subject to employer’s approval.

- All luminaries shall be supplied, installed and tested by the electrical sub-contractor.

- Outdoor lighting shall be controlled from an automatic photo cell.

- Lighting control switches shall be flush pattern with white finished plates.

    - The outdoor SPGP flood lights/perimeter security lighting to be achieve the recommended luminaries and mounted on concrete poles.

    - Socket outlets to be mounted at 300 mm above floor level in the office, guard house and control room.

    - Conduit cast into the building structure shall be of the heavy-duty PVC type. PVC conduits shall not be fixed to the surface of the structure.

  - AC Installation

The contractor to supply the ACs in the control room. The Contractor shall supply and install a minimum of two number AC units, including wiring and all necessary accessories. The number of ACs and its capacity shall be determined by calculations and design will be based on the equipment manufacturers ratings adopted and the rooms requirement (Including Lithium-Ion Batteries) and subject to approval by the employer.

  - Fire Safety Facilities

    - Portable fire extinguishers shall be provided under this Contract. Portable, wall mounted, hand held extinguishers shall be 6kg pressurized control discharge Bromochlorodifluoromethane (BCF) units in the office and control room. The number of units within the Control room and office shall be a minimum of 3 Number.

    - A minimum of 1 No. 13 kg pressurized control discharge BCF units shall be provided in the SPGP area.

    - The body of the extinguisher shall be seamless, welded and brazed as appropriate.

    - The extinguisher shall be capable of being released by means of a lever-operated valve provided with a safety pin.

    - Extinguishers shall be capable of controlled partial discharge.

    - The type shall be of that recharge unit that is locally available.

    - The extinguishers shall be wall mounted and attached and located in a manner affording quick release from the supporting bracket. They shall be installed so that the top of the extinguisher is not more than 1.5meters above the floor. In no case shall the clearance between the bottom of the extinguisher and the floor be less than 0.1 meter. The extinguishers shall be positioned so that the

instructions for operation face outwards.

    - BESS to be housed in one room in the control room. The battery room shall have an automated fire detection, prevention and suppression system fitted with a suitable dry aerosol agent to put-out Lithium-Ion battery fires. The system shall include smoke detectors, horn strobes and other components required to enable it function properly and suppress fires while preventing unintended release. Suitable Fire protection and suppression system shall be designed for BESS in line with IEC or international requirements/specifications regulation as applicable and system requirement considering project site.

    - The fire safety design shall be subject to approval by the employer. The contractor shall train the local staff on use of the installed system.

Part II

#### 14. Detailed Technical Specification and Requirements

The proposed project under this tender for setting the solar PV hybrid power plant shall broadly follow technical specifications given below.

- These specifications describe the requirements for the equipment. Tenderers are requested to submit with their offers the detailed specifications, drawings and catalogues, for the products they intend to supply. The details in the provided catalogues SHALL be used in the tender evaluation for specification compliance.

- Tenderers must indicate on the specifications sheets whether the equipment offered comply with each specified requirement.

- All the dimensions and capacities of the equipment to be supplied SHALL not be less than those required in these specifications.

The Tenderer shall indicate in the technical specification of each component brand name, model and country of origin. Comparative specification should indicate any derivations from technical parameter, design, or functional description of tender specification

##### 14.1 Documentation and Instructions (Required during installation and commissioning)

| No. | PRODUCTS DOCUMENTATION AND SPECIFICATION | BIDDERS RESPONSE |
| --- | --- | --- |
| 1 | Product description and data sheets, manufacture description, and operation manual |  |
| 2 | Installation instructions |  |
| 3 | Connection plans, single line diagram |  |
| 4 | Commissioning instructions, manual for start and stop operation, commissioning protocol |  |
| 5 | Operating instructions, do´s and don´ts |  |
| 6 | Maintenance instructions, maintenance interval, maintenance effort, necessary staff |  |
| 7 | Error sources, error diagnosis and troubleshooting instructions |  |

##### 14.2 Solar Photovoltaic Modules

| ITEM | REREC’S REQUIREMENT FOR SOLAR MODULE |  |  |  | BIDDERS RESPONSE |
| --- | --- | --- | --- | --- | --- |
|  | Name of Manufacturer, Brand Name |  |  |  |  |
|  | Model No. |  |  |  |  |
|  | Cell type |  | Mono crystalline |  |  |
|  | Originality Verification system |  | Barcode or Serial number with batch number |  |  |
|  | Solar cells encapsulated in EVA (ethylene-vinyl acetate); anti- reflection coating; Module on the front side protected by tempered, highly translucent glass. |  |  |  |  |
|  | Glass-foil laminated in anodized aluminum-frame |  |  |  |  |
|  | Wind load certification |  | 0.024 bars |  |  |
|  | Front glass |  | High transmission, low iron, Tempered glass |  |  |
|  | Weather resistant Junction box with 3 Bypass-diodes on the backside of the modules with protection class min. IP 67 rated |  |  |  |  |
|  | Wiring of the modules with pin-and-socket connector according to EN 50521 |  |  |  |  |
|  | Quantity of cells |  | state |  |  |
|  | Temperature coefficient PMPP: |  | <=-0.45%/C |  |  |
|  | Temperature coefficient Voc: |  | <=-0.27%/C |  |  |
|  | Temperature coefficient Isc: |  | <=0.05%/C |  |  |
|  | Operating temperature range: |  | -0°C < =T< =45 °C |  |  |
|  | Nominal operating cell temperature (NOCT) |  | 45+/- 2 °C |  |  |
|  | Module efficiency |  | at STC-conditions > 22% |  |  |
|  | Current at maximum power point (A) (maximum) |  | State |  |  |
|  | Voltage at maximum Power Point (V) (minimum) |  | State |  |  |
|  | Open Circuit voltage (Voc) |  | State |  |  |
|  | Short circuit current (Isc) |  | State |  |  |
|  | Minimum rating |  | 400W |  |  |
|  | 10 years product warranty |  |  |  |  |
|  | 25 years linear performance guarantee (90% up to 12 years and 80% up to 25 years) |  |  |  |  |
|  | CE- conformity, DVE GS, TUV quality certified for product |  |  |  |  |
|  | Horizontal and vertical assembly possible |  |  |  |  |
|  | High Mechanical load (acc. IEC 61215 (5400Pa superimposed load and 2400Pa suction load)) |  |  |  |  |
|  | Pre-cabled with MC4 Plug –connectors (IP 67) |  |  |  |  |
|  | Nominal power at IEC-Conditions (radiation 1000W/m2, Air-Mass 1.5 25°C) |  |  |  |  |
|  | Output cables |  | Minimum TUV 1x4.0mm SQ |  |  |
|  | Product certification | IEC 61215 (Ed.2) |  |  |  |
|  | Protection class | II/ IEC 61730 |  |  |  |
|  | Salt mist corrosion test | IEC 61701 (Ed. 2) |  |  |  |
|  | Documentation: English | Please indicate: |  |  |  |
|  | Power Tolerance | Positive power tolerance -0/+3% |  |  |  |
|  | Cell dimension (length x width) in mm |  |  |  |  |
|  | Module dimension (length x width x height) in mm |  |  |  |  |
|  | Module weight in kg |  |  |  |  |

14.3 Hybrid Inverter

| ITEM |  | DESCRIPTION | REREC MINIMUM SPECIFICATION |  | BIDDER RESPONSE |  |
| --- | --- | --- | --- | --- | --- | --- |
| Battery Input Data |  |  |  |  |  |  |
| 1 |  | Battery type | Li-ion |  |  |  |
| 2 |  | Nominal battery voltage (V) | Indicate(above 48V) |  |  |  |
| 3 |  | Max Charging Current(A) | 100 |  |  |  |
| 4 |  | Max Discharging Current(A) | 100 |  |  |  |
| 5 |  | No. of Battery Input | state |  |  |  |
| 6 |  | Max. Charge / Discharge Power (KW) | State |  |  |  |
| PV String Input Data (or DC-DC Converter) |  |  |  |  |  |  |
| 7 |  | Max. Input Power (KW) | 52 |  |  |  |
| 8 |  | Max. Input Voltage (V) | State |  |  |  |
| 9 |  | MPPT Operating Voltage Range (V) | 150-850 |  |  |  |
| 10 |  | MPPT Voltage Range at Nominal Power(V) | 500-850 |  |  |  |
| 11 |  | Start-up Voltage (V) | Indicate |  |  |  |
| 12 |  | Nominal Input Voltage (V) | State |  |  |  |
| 13 |  | Max. Input Current per MPPT (A) | 120 |  |  |  |
| 14 |  | Max. Short Circuit Current per MPPT (A) | 150 |  |  |  |
| 15 |  | Max. Back-feed Current to the Array (A) | indicate |  |  |  |
| 16 |  | Number of MPPTs Trackers | Indicate |  |  |  |
| 17 |  | Number of Strings per MPPT (based on current limit) | indicate |  |  |  |
| AC Output Data (On-grid) |  |  |  |  |  |  |
| 18 |  | Nominal Apparent Power Output to Utility Grid (VA) | State |  |  |  |
| 19 |  | Output Rated Active Power (W) | State |  |  |  |
| 20 |  | Max. Apparent Power Output to Utility Grid | 1.5 times of rated power,10s |  |  |  |
| 21 |  | Nominal Apparent Power from Grid (KVA) | State |  |  |  |
| 22 |  | Max. Apparent Power from Utility Grid(KVA) | State |  |  |  |
| 23 |  | Nominal Output Voltage (V) | 400, 3L / N / PE |  |  |  |
| 24 |  | Output Voltage Range (V) | 312~460 (AS) / 318~497 |  |  |  |
| 25 |  | Nominal AC Grid Frequency (Hz) | 50 |  |  |  |
| 26 |  | AC Grid Frequency Range (Hz) | 47~52 (AS) / 47.5~51.5 |  |  |  |
| 27 |  | Max. AC Current Output to Utility Grid (A) | 76 |  |  |  |
| 28 |  | Max. AC Current from Utility Grid (A) | 100 |  |  |  |
| 29 |  | Max. Output Fault Current (Peak& Duration) (A) | 156A@150us |  |  |  |
| 30 |  | Inrush Current (Peak & Duration) (A) |  | 160 |  |  |
| 31 |  | Nominal Output Current (A) |  | 72.5 |  |  |
| 32 |  | Output Power Factor |  | -1(Adjustable from 0.8 leading to 0.8 lagging) |  |  |
| 33 |  | Max. Total Harmonic Distortion |  | <3% |  |  |
| 34 |  | Generator input/Smart load/Ac Couple current |  | Indicated |  |  |
| Efficiency |  |  |  |  |  |  |
| 35 |  | Max. Efficiency |  | 97.60% |  |  |
| 36 |  | Max. Battery to Load Efficiency |  | 97.20% |  |  |
| Protection |  |  |  |  |  |  |
| 37 |  | DC Insulation Resistance Detection |  | Integrated |  |  |
| 38 |  | Residual Current Monitoring Unit |  | Integrated |  |  |
| 39 |  | Anti-islanding Protection |  | Integrated |  |  |
| 40 |  | DC Reverse Polarity Protection |  | Integrated |  |  |
| 41 |  | AC Overcurrent / Overvoltage Protection |  | Integrated |  |  |
| 42 |  | AC Short Circuit Protection |  | Integrated |  |  |
| 43 |  | DC / AC Surge Arrester |  | Type II (Type I Optional) |  |  |
| 44 |  | DC / AC Switch |  | Integrated |  |  |
| 45 |  | Emergency Power Off |  | Integrated |  |  |
| 46 |  | Rapid Shutdown |  | Optional |  |  |
| 47 |  | Remote Shutdown |  | Integrated |  |  |
| General Data |  |  |  |  |  |  |
| 48 |  | Operating Temperature Range (°C) |  | -20~+60°C (>45°C |  |  |
|  |  |  |  | derating) |  |  |
| 49 |  | Relative Humidity |  | 0~95% (Non-condensing) |  |  |
| 50 |  | Max. Operating Altitude (m) |  | 4000 |  |  |
| 51 |  | Cooling Method |  | Fan Cooling |  |  |
| 52 |  | User Interface |  | LCD & LED & APP |  |  |
| 53 |  | Communication with BMS |  | RS485/CAN |  |  |
| 54 |  | Communication with Meter |  | RS485/CAN |  |  |
| 55 |  | Weight (Kg) |  | Indicate |  |  |
| 56 |  | Dimension W × H × D -in (mm) |  | Indicate |  |  |
| 57 |  | Noise Emission (dB) |  | 50 |  |  |
| 58 |  | Topology |  | Transformerless |  |  |
| 59 |  | DC / AC Connector |  | NC |  |  |
| 60 |  | Protective Class |  | I |  |  |
| 61 |  | Environmental Category |  | 4K4H |  |  |
| 62 |  | Storage Environment (°C) |  | -30~+60°C |  |  |
| 63 |  | Overvoltage Category |  | DC II / AC III |  |  |
| 64 |  | The Decisive Voltage Class (DVC) |  | C |  |  |
| 65 |  | Installation Style |  | Wall -Mounted |  |  |

##### 14.4 Battery Storage

| ITEM | REREC MINIMUM SPECIFICATION FOR THE BATTERY STORAGE |  | BIDDERS RESPONSE |
| --- | --- | --- | --- |
| 1 | Type of battery | Lithium-ion Phosphate |  |
| 2 | Name of manufacturer, Brand Model, Type name, |  |  |
| 3 | Type of technology |  |  |
| 4 | State of charge | Pre-charged |  |
| 5 | DC-Voltage | V/cell |  |
| 6 | DC-Voltage battery bank | V |  |
| 7 | Qty of cells | State |  |
| 8 | String configuration | Provide drawing |  |
| 9 | Number of Strings | State |  |
| 10 | Rated energy capacity/string | 100 kWh (Max) |  |
| 11 | Total rated Capacity (kWh) | 400 kWh (Minimum) |  |
| 12 | Energy (kWh) per Piece | 10 kWh (Max.) |  |
| 13 | Nominal Voltage (V） | ≥48 |  |
| 14 | Discharge Voltage (V） | indicate |  |
| 15 | Charging Voltage (V) | indicate |  |
| 16 | Max. Charging Current (A) | 100A |  |
| 17 | Max. Discharge Current (A ） | 100A |  |
| 18 | Storage temperature | 0~35℃ |  |
| 19 | Max. working altitude (M） | 4000M |  |
| 20 | Relative humidity | 0~95% non-condensing |  |
| 21 | Installation | Frame |  |
| 22 | Ingress protection | IP21 |  |
| 23 | Operating temperature | -25℃~55℃ |  |
| 24 | Designed according | DIN 40736 |  |
| 25 | Certification | UN 38.3, IEC 62619 |  |
| 26 | Self-discharge per month at 20° degrees | < 3% |  |
| 27 | Cycles at 80% DoD(according to IEC 896- 1) | > 5000@ 25℃ 80% (Minimum) |  |
| 28 | Max. DOD in operation | > 90 % |  |
| 29 | At least 10 years without losing more than 20% of the rated capacity |  |  |
| 30 | Battery management system (BMS) | Cell balancing |  |
| 31 |  | Protection overcharge, over-discharge each cell |  |
| 32 |  | Protection over and under temperature |  |
| 33 |  | Isolation of battery if any of the above occur |  |
| 34 |  | Alert if there is a failure |  |
| 35 |  | Communication with Battery inverter |  |
| 36 | BMS Communication interface | RS485,Ethernet |  |
| 37 | BMS Communication protocol | Modbus RTU, Modbus TCP |  |
| 38 | Warranty | 5 Years |  |
| 39 | Performance guarantee | 10 Years |  |

##### 14.5 Diesel Generator

| ITEM | SPECIFICATION OF 3-PHASE DIESEL GENERATOR |  | BIDDERS RESPONSE |
| --- | --- | --- | --- |
| 1 | Name of manufacturer, Brand name, Model, Type |  |  |
| 2 | Type of Diesel generator | Synchronous generator |  |
| 3 | Diesel Generating Set, water cooled, incl. sound and weather proofed canopy; Stationary version, incl. lifting hook; tropicalized, ready for use, fitted as complete unit on a rigid base frame (e.g. skid mounted), consisting of Motor, Alternator, Battery, Fuel tank and separate switch board and accessories mentioned below. Norms and reference values to be followed: VDE, EN, DIN, ISO or equivalent norms. In p articular VDE 0100, Part 551/560, VDE 0108, DIN ISO 8528, DIN ISO 30 46 and/or norms or other guidelines as may be mentioned in the present specification. |  |  |
| 4 | Output power (Tolerance + 2,5 / - 0 KVA) taking into consideration the environmental conditions | 50 kVA |  |
| 5 | Output power | 50 kVA |  |
| 6 | Fuel consumption at 50 % load | l |  |
| 7 | Fuel consumption at 80 % load | l |  |
| 8 | Overall efficiency | % |  |
| 9 | Site of operation / Purpose / Environmental conditions Outdoor installation up to +35°C, Altitude see, air humidity 70 % |  |  |
| 10 | Environmental conditions | Ambient temperature up to +35°C |  |
| 11 | CE declaration of conformity by the manufacturer exists. Please attach the document to your offer. |  |  |
| 12 | Welded sectional steel base frame, warp resistant, lifting hook on each corner for easy lifting |  |  |
| 13 | Motor, Norms and reference values: ISO 3046, DIN 6271, BS 5514 |  |  |
| 14 | Type: Diesel, direct injection, forced oil lubrication, fuel transfer pump |  |  |
| 15 | Revs: 1500 rpm |  |  |
| 16 | Speed regulation: electrical |  |  |
| 17 | Cooling: water cooled, considering a surrounding temperature of 40°C |  |  |
| 18 | Alternator, battery charging: Integrated 24V |  |  |
| 19 | Starter motor: integrated 24V |  |  |
| 20 | Starter battery fitted to the aggregate incl. hood, 24V, dry pre-charged |  |  |
| 21 | Fuel tank: steel, fitted to the frame, incl. fuel level gauge. Tank capacity: at least for a 8 hours run under maximum continuous output. |  |  |
| 22 | Motor brand and designation, Model and Type |  |  |
| 23 | Number of cylinders and cubic capacity |  |  |
| 24 | Fuel tank capacity |  |  |
| 25 | Oil capacity |  |  |
| 26 | Motor capacity as per ISO 3046-7 based on 25°C intake temperature, 25°C cooling water intake temperature, 1.000 mbar air pressure, 30% air humidity – (KW) |  |  |
| 27 | Motor capacity as per ISO 3046 in reference of the environmental conditions, mechanical (KWm) |  |  |
| 28 | Motor capacity as per ISO 3046 in reference to the environmental conditions, electrical (KWe) |  |  |
| 29 | Fuel consumption as per ISO 3046-1 including attached pumps. Lower fuel heating value 42.700 KJ/kg Tolerance + 5% at PRP 100% load in g/KWh |  |  |
| 30 | Lubrication oil consumption (ltr/h) under standard conditions |  |  |
| 31 | Alternator brand, model, type |  |  |
| 32 | Efficiency factor of Alternator |  |  |
| 33 | Alternator: Norms and reference values: VDE 0530, BS 4999, UTE NFnC 51.111, IEC 34.1, NEMA MG 21 |  |  |
| 34 | Three-phase current alternator as per VDE 0530, internal pol machine with damping winding, self-regulating, self-starting |  |  |
| 35 | Voltage rigidity: max 5 % |  |  |
| 36 | Nominal voltage: Per phase 240V alternating current, 415 V three-phase current |  |  |
| 37 | Frequency: 50 Hz |  |  |
| 38 | Power factor: cos phi 0,8 |  |  |
| 39 | Insulation class: H or F |  |  |
| 40 | Isolation good for tropic climate |  |  |
| 41 | Radio interference suppression according to VDE 0875 “N” |  |  |
| 42 | Protection class DIN 40050, IP 23 |  |  |
| 43 | G3 Classification according to DIN ISO 8528 |  |  |
| 44 | Exhaust system, sound protection |  |  |
| 45 | Weather and sound proofed canopy incl. exhaust silencer. High corrosion resistance: stainless covered with zinc and made in dichromate. Large doors allow easy access to the generator set for service and monitoring purposes. Lockable doors with one window showing the control panel, fully assembled for immediate use. Exhaust system fully integrated (inner mounted).sound protection LWA below 89 dB (A)pW. Emergency stop button is accessible from outside enclosure. |  |  |
| 46 | Please indicate: |  |  |
| 47 | Acoustic power (LWA) [dB (A)] |  |  |
| 48 | Acoustic pressure level at 1 m distance |  |  |
| 49 | Acoustic pressure level at 7 m distance |  |  |
| 50 | Acoustic pressure level at 10 m distance |  |  |
| 51 | Control fittings / Measuring Instruments / Switch board |  |  |
| 52 | Switch cabinet - vibration proof – fitted to the steel base frame - Digital control panel |  |  |
| 53 | Motor protection accessories (Oil pressure, water temperature, excessive revs) Generator protection switch, thermic-magnetic overload protection, protection of Instruments and indicators |  |  |
| 54 | Battery-charging control light, oil-pressure warning light, excessive temperature warning light, light test, excessive revs alarm, false start light, emergency-off light, central warning light |  |  |
| 55 | Measuring instruments, switches; Ampere, Volt, frequency, operation hours counter, Energy production, emergency “off” button, manual mode switch |  |  |
| 56 | 30 m reinforced electrical cable for electrical power supply, under- or above ground use |  |  |
| 57 | 5 m yellow-green cable with ground pin |  |  |
| 58 | Labeling of all components in English language |  |  |
| 59 | Please indicate: |  |  |
| 60 | Dimensions of one unit: (length x width x height) |  |  |
| 61 | Weight of one unit in kg (without any fillings) |  |  |
| 62 | Documentation |  |  |
| 63 | Manual for installation, commissioning and use plus a spare parts catalogue for each part of the generator (motor, generator, switch board, wiring diagram) in English |  |  |
| 64 | Spare parts / Maintenance parts / Consumables covering 1000 hrs of operation |  |  |
| 65 | 2 pcs. Oil filters |  |  |
| 66 | 1 pcs. Air filter |  |  |
| 67 | 2 pcs. Fuel filter ext. |  |  |
| 68 | 1 set of seals, screws, nuts, etc, for 1000 hrs of operation |  |  |
| 69 | 1 pcs. V-belt |  |  |
| 70 | Standard tool set |  |  |
| 71 | Standard tool set to provide maintenance and small repairs up to 1000 hrs of operation |  |  |

14.6 LAPTOP

| ITEM | DESCRIPTION | REREC’S REQUIREMENT | TENDERER RESPONSE |
| --- | --- | --- | --- |
| 1 | Name of the Manufacturer |  |  |
| 2 | RAM | 16GB |  |
| 3 | Processor | Core i7 |  |
| 4 | Storage | SSD 512GB |  |
| 5 | Processing Speed | 4.6 GHz |  |
| 6 | Graphic Card | 8 GB |  |
| 7 | Operating System | Windows 11 |  |

##### 14.6 Data Monitoring

| ITEM | SPECIFICATION OF MONITORING SYSTEM |  |  | BIDDERS RESPONSE |
| --- | --- | --- | --- | --- |
| 1 | Name of manufacturer, Brand name, Model, Type |  |  |  |
| 2 | Data logging and transmission of PV inverter data or charge controller | All inverter production data to be continuously transmitted via internet |  |  |
| 3 |  | Programmable data resoluti min: | on from 1 min - 60 |  |
| 4 |  | DC current, DC voltage |  |  |
| 5 |  | DC power, DC energy |  |  |
| 6. |  | AC current, AC voltage |  |  |
| 7 |  | AC power, AC energy |  |  |
| 8 |  | Ambient temperature (°C) |  |  |
| 9 |  | Solar radiation (W/m2) |  |  |
| 10 | Option | Transmission of inverter equivalent | data by GSM or |  |
| 11 | One radiation sensor (precision >90%) for global horizontal irradiance for the PV technology. Installed in shadow free position with access for regular cleaning. |  |  |  |
| 12 | One sensor corresponding with the monitoring system including to measure ambient temperature |  |  |  |
| 13 | Option: Three phase meters to be installed to measure power delivered to the loads |  |  |  |
| 14 | Data monitoring supply from DC power supply of installed battery storage with corresponding step down converter. |  |  |  |

##### 14.7 Balance of System (Required during installation)

| ITEM | SPECIFICATION OF BALANCE OF SYSTEM (BOS) |  | BIDDERS RESPONSE |
| --- | --- | --- | --- |
|  | The following material/Equipment will adhere to the prescribed standards |  |  |
| 1 | Outdoor cabinets | UV and water resistant material, min IP 54 |  |
| 2 | Cabinets/enclosures (where applicable shall contain) | MCB |  |
| 3 |  | MCCB |  |
| 4 |  | SPDs, class II IEC 61643-11 |  |
| 5 |  | Operating temperature up to |  |
| 6 |  | Non-metallic fiberglass enclosures with clear polycarbonate covers |  |
| 7 | Electricity meter | Bidirectional, 3 phase class 0,5 |  |
| 8 | AC cabling- Inverter distribution to grid connection point | IEC 60364 |  |
| 9 |  | KS 04-192: 1988 |  |
| 10 |  | KS 04 -194: 1990 |  |
| 11 |  | KS 04 -187/188 |  |
| 12 |  | KS 04 -290: 1987 |  |
| 13 | Lightning protection | IEC 62305 |  |
| 14 | Miscellaneous accessories (if applicable) Conduit outlets and junction boxes | KS 04-179: 1983 |  |

| ITEM | SPECIFICATION FOR DC CABLING AND CONNECTORS The following material/Equipment will adhere to the prescribed standards |  | BIDDERS RESPONSE |
| --- | --- | --- | --- |
| 1 | Fine copper for PV string connection to inverter |  |  |
| 2 | Outdoor use TUV approval Nr. | TUV PfG 1169/08.2007 |  |
| 3 | Ozone resistant | EN 50396 |  |
| 4 | Flame retardant | IEC/EN 60332-1-2 |  |
| 5 | UV resistant | HD 605/A1 |  |
| 6 | Halogen free | EN 50267-2-1, EN 60684-2 |  |
| 7 | Acid + Alkaline resistant | IEC /EN 60811-2-1 |  |
| 8 | Low corrosively of gases | EN 50267-2-2 |  |
| 9 | Weather resistant | HD 605/A1 |  |
| 10 | DC wiring losses | Total DC wiring losses max. 1,5% |  |
| 11 | DC connectors | EN 50521 |  |
| 12 |  | Crimped according to manufacturer instructions using only certified tools |  |

##### 14.8 Commissioning and training

| ITEM | COMMISSIONING AND TRAINING ON SITE The following shall be carried out during commissioning | BIDDERS RESPONSE |
| --- | --- | --- |
| 1 | Complete commissioning and trial operation of the system. Please indicate. |  |
| 2 | Training on the operation of the power plant components, maintenance and monitoring of the system. General information, system description and scope of delivery. Please indicate |  |

#### 15. Performance Guarantees

| ITEM | PERFORMANCE GUARANTEES | BIDDERS RESPONSE |
| --- | --- | --- |
| 1 | Upon commissioning of the solar PV hybrid power plant and 1 month of operation the final acceptance of the solar PV hybrid system will be confirmed after. During this one month the contractor should fix all installation problems that arise. |  |
| 2 | After final acceptance, a 12-month defect liability period shall commence. |  |

PART II

Sub-Station Specifications

The Scope of the project;

A mini-grid comprising of photovoltaic solar (PV) generation, battery storage and a generator backup. The entire generation is to be synchronized and managed by the solar PV controllers at 415Volts and stepped to 11KV distribution network.

Protection at the HV (High Voltage) side shall be done with the 11KV Circuit breaker complete with its Control and protective relay panel and the LV protection up to the step up transformer to be enhanced by the feeder which shall be installed in the 20feet air conditioned containers provided by the contractor.

Specifications For 415 V Ac Metal-Clad Switchgear Board

- General Specifications

- Scope

This Specification covers the Design and Engineering, Manufacture, Testing at The Manufacturer’s Factory, painting, packing for transport, insuring, shipping, delivering to the port of Kenya, landing, customs clearing, Local Transportation and Delivery to Site, Unpacking, Erection, Test and Commissioning of 415 V AC Indoor Metal Clad Switchgear Panels.

Subsequent paragraphs will give detailed descriptions and requirements for the Switchgear Panels, including Air Circuit Breakers, Current Transformers, Protection Relays, Metering, Measuring, Indicating and Control devices and other equipment/Devices, specified herein.

- Standards

Ratings, characteristics, tests and test procedures, etc. for the 415V AC Metal-Clad Switchgear Board and all the Protection Relays, Measuring and Indicating Instruments and the control and monitoring devices and Accessories, including Current transformers shall comply with the provisions and requirements of the standards of the International Electro- technical Commission

(IEC), and also relevant ANSI Standards where Specified.

The latest revision or edition in effect at the time of Bid Invitation shall apply. Where references are given to numbers in the old numbering scheme from IEC it shall be taken to be the equivalent number in the new five-digit number scheme. The Bidder shall specifically state the Precise Standard, complete with identification number, to which the various equipment and materials are manufactured and Tested. The Bid Document may not contain a full list of standards to be used, as they only are referred to where useful for clarification of the text.

- Service Conditions

From the geographical condition, the area where the switchgear panels shall be installed is categorized into the tropical climate zone.

In choosing materials and their finishes, due regard shall be given to the humid tropical conditions under which the switchgear panels shall be called upon to work. The Manufacturer of the Switchgear panels shall submit details of his usual practice of tropicalization which have proven satisfactory for application to the Switchgear panels and associated equipment to prevent Rusting and Ageing in the Tropical Climate Zone. The Applicable standards for tropicalization shall be listed.

- Climatic Conditions & Geo-Reference

Unless otherwise specifically stated in Particular Technical Specifications, any equipment or component or assembly shall be designed for the following service conditions:

Parameter

Ambient air temperature	Max	Min

Outdoor	+40°C	-1°C

Indoor		+40°C	-1°C

24 hour average maximum	+30°C	-1°C

Relative humidity	90 -100%

Height above sea level	1000 m

EMC Class (IEC 61000)	Industrial environments Seismic coefficient		1.5

Rainfall conditions

Average	800-1700 mm/year

Maximum	160mm in 24 hrs

Annual mean isokeraunic level	Max 180 thunderstorm days

Pollution (IEC 60815)	Heavy: class II

Geo-Reference Latitude (o) Longitude (o) Altitude (m) a.s.l.

Switchgear room Temperature

The Switchgear shall be installed in a room without Air conditioning but with ventilation to allow natural cooling. Therefore, All the Protection and control devices employed shall be capable of operating in this environment without failure for their designed life time. Particularly the power supply modules of the Protection and Control devices shall be designed for minimum heat generation and effective heat dissipation to ensure that the temperature of these devices enclosed in the relay panels at the above listed Ambient temperatures shall not exceed the Maximum operating temperature of the device.

- Tropicalization

- All equipment must be designed for operations in the severe tropic climate conditions and fully comply with climatic aging tests as per IEC 60932- class 2

Metals:

Iron and Steel are generally to be painted or galvanized as appropriate. Indoor parts may alternatively have chromium or copper-nickel plates or other approved protective finish. Small iron and steel parts (other than rustles steel) of all instruments and electrical equipment, the cores of electromagnets and the metal parts of relays and mechanisms shall be treated in an appropriate manner to prevent rusting.

Screws, Nuts, Springs, Etc.

The use of Iron and steels shall be avoided in instruments and electrical relays wherever possible. Steel screws shall be zinc, cadmium or chromium plated or where plating is not possible owing to tolerance limitations, shall be of corrosion resisting steel. Instrument screws (except those forming part of a magnetic circuit) shall be of brass or bronze. Springs shall be of non- rusting material, e.g., phosphor-bronze or nickel silver, as far as possible.

- Working Stress And Equipment/Apparatus Design

- General

The design, dimensions and materials of all parts shall be such that they will not suffer damage under the most adverse conditions nor result in deflections and vibrations, which might adversely affect the operation of the equipment. Mechanisms shall be constructed to avoid sticking due to rust or corrosion.

The equipment and apparatus shall be designed and manufactured in the best and most substantial and workmanlike manner with materials best suited to their respective purpose and generally in accordance with up-to-date recognized standards of good practice. The equipment shall be designed to cope with 0.10G acceleration of seismology on the centers of gravity. All equipment shall be designed to minimize the risk of fire and consequential damage, to prevent ingress of vermin and dust and accidental contact with electrically energized or moving parts. The switchgear panels shall be capable of continuous operation with minimum attention and maintenance in the exceptionally severe conditions likely to be obtained in a tropical climate and where the switchgear is called upon to frequently interrupt fault currents on the system and also where the duty of operation is high.

- Strength and quality

Liberal factors of safety shall be used throughout, especially in the design of all parts subject to alternating stresses or shocks.

- Design data low voltage equipment

Low voltage equipment and installation shall be designed in accordance with EMC directives. The rating and design criteria for low voltage equipment shall be as follows:

- AC Supply Rating system

| Rated voltage between phase | 415 V |
| --- | --- |
| Connection type | 3ph 4wire |
| Rated voltage between phase to earth | 240 V |
| Grounding system | Solid Earthing |
| Frequency | 50 HZ |
| Voltage variation | +/-10% |
| Frequency variation | +/-2% |
| Power frequency 1 min, Test Voltage | 3 kV |

The three-phase supply shall be used for power circuit and the single- phase supply for lighting, indication, motor controls and similar small power circuits. Unless otherwise specified, the equipment provided under this Tender is to be capable of reliable operation at voltages as low as 85% of the rated voltage, and to withstand continuously up to 110% supply voltage above the rated value of 240V single phase or 415V AC three phase.

- DC Auxiliary Supply Rating

| Equipment/Device Rated voltage | 24V DC |
| --- | --- |
| Connection type | 2 wire |
| Voltage variation | 18-36 V DC |

The Auxiliary DC Supply shall be used for controls, indication, alarm, protection relays, and Circuit breaker tripping and closing circuit, e.t.c.

All equipment and apparatus including the Circuit Breakers, Protective relays, Control Devices and Accessories, Measuring and Indicating Instruments and electronic equipment shall be capable of satisfactory operation at 80% to 125% of the rated supply voltage.

- Basic Requirements For Electrical Equipment

All materials supplied under this Contract shall be new and of the best quality and of the class most suitable for working under the conditions specified. They shall withstand the variations of temperature and atmospheric conditions arising under working conditions without distortion, deterioration or undue stresses in any parts and also without affecting the suitability of the various parts of the Works for which they were designed.

- Electrical controls, auxiliaries and power supplies

- Responsibility for electrical control and auxiliaries

The Manufacturer shall provide all control, indication, alarm and protection devices and all auxiliary equipment with wiring and interconnecting cable which are integral parts of or are directly associated with or mounted on the Switchgear panels to be supplied under this Tender. The design of Protection and Control schemes for the switchgear panels shall be subject to approval by the Employer.

- Operation and control

Interlocking devices shall be incorporated in the control circuit to ensure Safety, and Proper sequence and correct operation of the equipment.

- Measuring instruments

- All measuring instruments, including energy meters, shall be of flush-mounted, back-connected, dust-proof and heavy-duty switchboard type. Each measuring instrument shall have a removable cover, either transparent or with a transparent window. Each instrument shall be suitable for operation with the instrument transformers detailed in this specification, under both normal and short-circuit conditions.

- For analog type instruments, scale plates shall be of a permanent white circular or rectangular finish with black pointer and markings. The scale range shall be determined from the current transformer and voltage transformer ratios and is given in the detailed specifications for each instrument.

All measuring instruments of analog type shall be approximately 110mm2 enclosures and shall be provided with clearly readable long scale, approximately 240 degrees. The maximum error shall be not more than one and a half (1.5) percent of full-scale range.

- Indicating lamps

Indicating lamp assemblies shall be of the switchboard type, insulated for 24 V D.C. service, with appropriately colored lens and integrally mounted resistors for 110-volt service. The lens shall be made of a material, which will not be softened by the heat from the lamps.

For the Circuit Breakers,	Red indicating lamps shall be used for “ON” position,

green lamps for “OFF” position Indication and Amber for Transition

- Nameplate and Escutcheon Plates

- Each cubicle, panel, meter, switch and device shall be provided with a nameplate or escutcheon plate for identification with English description and also where appropriate the IEC Number on the front of the panel directly below each device as appropriate. On the inside of the control compartment of the switchgear panel, a yellow label, engraved in Black Letters and Numbers shall be fixed below each device. The Device Name/Number fixed on the inside of the control compartment shall correspond to the Name/Number used in the drawings. Each equipment shall be provided with a rating plate containing the necessary information specified in the relevant IEC standards.

- The plates shall be made of weatherproof and corrosion-proof materials and shall not be deformed under the service conditions at the site. The entries on the plates shall be indelibly marked by engraving with black letter on a white background.

- Wiring

- General

- All wiring inside the switchgear panel shall be done with PVC insulated wire not less than 2.5 sq.mm, flexible cable. A suitable wiring duct system firmly fixed on the panel and having covers shall be installed for all inter-panel and front-to-rear panel wiring as well as for wiring within the panels, which will provide easy access for inspection and replacement of the wires.

- Wiring between terminals of the various devices shall be point to point. Splices or tee connection will not be acceptable. Wire runs from the duct to the device shall be neatly trucked or clamped.

- Exposed wiring shall be kept to a minimum, but where used, shall be formed into compact groups suitably bound together and properly supported.

- Instrument transformer secondary circuits shall be grounded only on the Terminal Block in the Control Compartment. Cable supports and clamp type terminal lugs shall be provided for all incoming and outgoing power wiring terminated at each panel. All wiring conductors (wires) shall be marked at each point of termination onto the terminal block or device. These wire markers shall be of an approved type and permanently attached to the conductor insulation. The method of ferruling shall be subject to approval by the Employer; It is however preferred that the Wire marker (ferrule) correspond to the device terminal Number of the device or the Terminal Block Number where it is terminated.

- Phase arrangement

The standard phase arrangement when facing the front of the panel shall be R-S-T- N, and P-N from the left to right, from top to bottom, and front to back for A.C three- phase and single-phase circuits. For DC circuit it shall be N-P from left to right, P-N from top to bottom and front to back. All relays, instruments, other devices, buses and equipment involving three-phase circuit shall be arranged and connected in accordance with the standard phase arrangement wherever possible.

- Terminal blocks

- Terminal blocks for control wiring shall be rated not less than 600V AC.

- Each Individual Terminal Block shall be marked with a distinctive Number, which shall be the same Number used in the drawings, for identification purposes. The TB number shall be engraved in black numbers in white background.

- Each set of terminal Block shall be identified by a label to distinguish it from another set of terminal block with similar Numbers for the individual terminal blocks. The labels used will match those used in the drawings.

- Equipment And Switchgear Earthing

- General

All the Compartments including the hinged doors of the Switchgear Panels and all the earthing points of the equipment installed/mounted in the Switchgear panels shall be connected to the grounding conductor at the bottom of the panel for external connection to the substation earthing System.

Earthing conductors shall be of annealed high conductivity copper. The earthing conductor on the primary equipment such as the Earth Switch and also for inter-panel earth-bonding as well as for external connection to the substation Earthing – grid shall be adequate to carry the rated switchgear short-circuit current of 65kA for 1 seconds.

- Materials And Workmanship

- General

Materials shall be new; the best quality of their respective kinds and such as are usual and suitable for work of like character. All materials shall comply with the latest issues of the specified standard unless otherwise specified or permitted by the Employer.

Workmanship shall be of the highest class throughout to ensure reliable and vibrations free Operations. The design, dimensions and materials of all parts shall be such that the stresses to which they may be subjected shall not cause distortion, undue wear, or damage under the most

severe conditions encountered in service.

All parts shall conform to the dimensions shown and shall be built in accordance with approved drawings. All joints, datum surfaces and meeting components shall be machined and all castings shall be spot faced for nuts. All machined finished shall be shown on the drawings. All screw, bolts, studs and nuts and threads for pipe shall conform to the latest standards of the International Organization for Standardization covering these components and shall all conform to the standards for metric sizes

All materials and works that have cracks, flaws or other defects or inferior workmanship will be rejected by the Employer.

- Assembly

Necessary items of equipment shall be assembled in the factory prior to shipment and Routine tests shall be performed by the Manufacturer as per the requirements of the latest issue of IEC as specified under each equipment in these specifications to demonstrate to the satisfaction of the Employer that the Switchgear panels comply with the requirements of the relevant IEC standards.

- Casting

Casting shall be true to pattern, of workmanlike finish and of uniform quality and condition, free from blowholes, porosity, hard spots, shrinkage defects, cracks or other injurious defects, shall be satisfactorily cleaned for their intended purpose.

- Operational Details

Instructions shall be engraved on the switchgear panel, on the circuit breaker compartment describing in simple steps how to carry out correct and safe Isolation, racking-in and switching operations on the circuit breaker. Similar details should be provided for the operation of the earth switch.

- Protection, Cleaning And Painting

All outside panel surfaces shall be primed, filed where necessary, and given not less than two coats of synthetic undercoat. The finishing coat for the indoor installations shall be gloss paint.

Primer shall be applied to surfaces prepared in accordance with the plant manufacturer’s instructions. The surface shall be wiped clean immediately prior to applying the paint. The primer and finish coats of paint shall be applied using the methods and equipment recommended by the manufacturer.

No painting or protection is required for finished or unfinished stainless steel parts.

The humid and tropical conditions shall be taken into account on selection of the paints and painting procedure.

- Drawings

- Before starting manufacture of the Switchgear panels, dimensioned drawings and data showing all significant details of the equipment and materials to be used shall be submitted to the Employer for approval. Four 4 weeks shall be allowed for discussions between the manufacturer and the employer leading to final Approval of the drawings by the Employer. Manufacturing of the switchgear panels shall not commence under any circumstances without receipt of Approved drawings by the Manufacturer from the employer.

- The drawings shall be modified as necessary if requested by the Employer, and resubmitted for final approval.

- The manufacture of the switchgear shall then proceed strictly in accordance with the Approved drawings and also in accordance with the Detailed specifications as contained herein. Where conflict may arise between the specifications and the approved drawings, the Specifications will take precedence, unless it’s specifically indicated in writing on the Approved drawings that the conflicting clause in the specifications is superseded, or where following discussions between the Manufacturer and the employer, the employer gives approval in writing to supersede the conflicting clause in the specifications.

- It is to be understood, however, that approval of the drawings will not relieve the manufacturer of any responsibility in connection with the works that the switchgear will fully comply with the relevant IEC/ANSI standards and with these specifications.

- All drawings submitted for approval or sent to the Employer for any other reason shall be in hard copy form and shall be sent by courier. Drawings for Approval shall not by any means be forwarded via e-mail or any other media except in hard copy form.

Following completion of the manufacture of the switchgear Panels, the manufacturer shall carry out the following Checks and Tests before Inviting the Employer for Factory Acceptance Tests. Dimensional checks for the switchgear Board and the Busbars. Primary Injection Tests to check correct connection of the current transformers to the relays and instruments and Measuring devices.

Electrical Functional Tests

Mechanical/Interlock

checks.

Any problems noted will be rectified and the switchgear panels shall only be shipped once the above tests and Checks are confirmed to be satisfactory.

Upon testing of the panels as in e) above the drawings will be edited to capture any minor wiring errors detected in order to produce the final construction drawings. A copy of the final construction drawings signed by the Manufacturer shall be send by courier to the employer before the panels are shipped.

All Protection and Control drawings shall be done on A4 - size paper. The function of each drawing shall be clearly indicated. Related drawings shall be arranged sequentially, and have the same drawing number but different sheet numbers. The drawings shall include the following; All Protection and Control drawings shall be done on A4 - size paper. The function of each drawing shall be clearly indicated. Related drawings shall be arranged sequentially, and have the same drawing number but different sheet numbers. The drawings shall include

the following;

- Ac single line drawing

- AC Schematics

- DC Schematics

- Functional Drawings

- Panel wiring and cable terminations and schedules

- Panel device layout drawing

- General layout drawings for the switchgear panels

- Relays and accessories list.

Five (5) Copies of Final As built drawings shall be supplied after commissioning of the Switchgear.

- Operating And Maintenance Instructions

The Contractor shall supply detailed instructions manuals concerning the correct manner of assembling/Installing/Erection, configuring, setting, Testing and Commissioning, operating and maintaining the equipment and devices constituting the Switchgear Board, including the board itself. The maintenance details of each component shall also be described, including the frequency of inspections and lubrication.

The instruction manual shall include a separate and complete section describing the normal and emergency operating procedures for the Switchgear, and shall include explanatory diagrammatic drawings to facilitate understanding the instructions.

The Manufacturer shall, in preparing the instruction manuals, take into account the lack of experience and familiarity of the Operators with this type of equipment.

The manual shall give specific information as to oil, grease, or any other materials needed for maintenance operations. This information shall include brand names and manufacturer’s numbers or designations for at least two brands available in Kenya, preferably manufactured in Kenya.

A complete set of the Operating and Maintenance manuals for All the Plant, Equipment and Accessories to be installed/mounted in the switchgear panels shall be sent to the Employer together with the Drawings for Approval. The operating and maintenance manuals shall be original copies printed by the manufacturer. Any illegible copies of the operating and maintenance manuals submitted shall be rejected by the employer.

Before Approval of Shipment of the switchgear Panels, Five (5) Copies of the Operating and Maintenance Instructions/Manuals shall be sent to the Employer by Courier. The operating and maintenance manuals shall be original copies printed by the manufacturer. Any illegible copies of the operating and maintenance manuals submitted shall be rejected

In addition, three (3) Soft copies of the manuals shall be sent to the employer by Courier.

- Testing At Place of Manufacture

The manufacturer shall be responsible for performing or for having performed all the required tests specified under the specification for the switchgear and all the Current Transformers, Protection Relays, Energy Meter, Measuring and Indicating instruments.

Tender documents shall be accompanied by copies of Type test and Routine test reports & certificates for similar rated equipment for the purpose of tender evaluation. Type test reports & certificates shall be certified by the National Standards and Testing Authority (NSTA) of the country of origin or by a third party Reputable Testing Authority. Where a body other than NSTA is used to certify the type-test reports, a copy of the certificate of accreditation shall be attached. Current contact information of the testing and certification authority shall be provided. Tenderers should note that this requirement is Mandatory.

Upon completion of the manufacturing process, routine tests shall be carried out as per the respective IEC standards of each equipment as follows:

- Circuit Breaker IEC 60298, IEC 60947

- Switchgear panels, IEC 60294

- Current Transformers, IEC 60044-1

- Voltage Transformer, IEC 60044-2

- Protection Relays and Measuring and Indicating Instruments, IEC 60255 & 51

Only Upon receipt of Authentic certified copies of the Routine Test Reports/certificates and special Tests shall the Employer give clearance for shipment of the Switchgear Board once all the other listed requirements on Drawings, Instruction and maintenance manuals and software are met.

- Software

One copy of each different type of Software in a CD Rom, for Protection Relays and other measuring and Control Devices whose Configuration and Settings is Software based and the connection Cable (Two for each type of device) shall be sent to the employer by courier before Approval for Shipment of the Switchgear Board is granted by the Employer. All the software indicated in the Technical Schedules shall be supplied. The software shall also be capable of downloading and analyzing data form the Relay/measuring device.

It shall be possible to load the software into at Least 2No. Different Laptop Computers without requirement for additional licenses, in order to facilitate Operations. Where additional licenses are required, the cost shall be considered to have been included in the bid.One b (1) set of hard cover manuals for each type of software Supplied providing detailed instructions for programming settings and configuration of the relays and other devices and downloading of data, shall be supplied with the switchgear.

- Spare Parts

The manufacturer shall furnish spare parts as listed in the specifications.

The spare parts supplied shall be packed or treated in such a manner as to be suitable for storage under the climate conditions at the Site for a period of not less than two years, and each part shall be clearly marked with the description and purpose on the outside of the package. The manner of storage shall be recommended by the manufacturer.

Spare parts so provided shall be delivered with the switchgear to the employer’s stores. Delivery of spare parts will not be deemed to be complete until the packages have been opened and their contents checked by a representative of the Employer.

- Detailed Specifications For 415 V Ac Metal-Clad Indoor Switchgear Panels

- Construction For Each Panel

- The whole switchgear equipment and components shall be designed and constructed in accordance with IEC 60298 and IEC 60947. The Board shall be complete with all the relevant components including, Busbars, Circuit Breaker, Cable Compartment, Instrument Transformers, Protection Relays, instruments and controls.

- The Switchgear Board, shall be constructed to 1P42 degree of Protection in accordance with IEC 60529. A type test Report for the Degree of Protection of the Switchgear panels from a third party Reputable Testing Laboratory or Certified by the National Standards and Testing Authority (NSTA) or a laboratory Accredited to the NSTA shall be submitted with the Tender for Evaluation Purposes.

- The switchgear panel or cubicle shall be built up of separate metal clad- compartmented cubicles with earthed metal partitions. The compartments shall be for busbar, cable connection and current transformer, Air circuit breaker, and Protection and Control compartments.

- The Air circuit breakers shall be mounted on an inbuilt carriage to facilitate Isolation and withdrawal of the Air Circuit Breaker. Where the carriage is fixed in the compartment and does not allow complete withdraw of the Air circuit breaker outside it’s compartment, then a purposely built Trolley shall be provided equipped with a lowering/raising gear to lower the Air circuit breaker to the floor, and to raise the circuit breaker to it’s compartment by one switching operator.

- The complete switchgear shall be such that the complete switchboard is of flush- front design.

- All the Protection Relays, Auxiliary Relays, Energy Meters Indication Lamps, Instruments, Control and selection switches and any other associated accessories will be mounted in the Protection and Control compartment. All the Protection Relays, Auxiliary Relays, Energy Meters Indication Lamps, Instruments, Control and selection switches and any other associated accessories will be mounted in the Protection and Control compartment.

- The cable compartment should have an anti vermin guard plate giving protection against rats, rodents etc.

- The Circuit breaker compartment door shall be provided with provisions for padlocking.

- The doors shall be capable of withstanding the effects of maximum internal arcing fault without being blown off and causing danger to other equipment/personnel.

- The busbar shall be single, three phase, air insulated. The primary busbars and connections shall be of high conductivity and electrolytic material, high grade copper, and shall be in unit lengths.

- Busbars, connections and their support shall be rated 800Amps continuously under ambient conditions and capable of carrying the short-time current associated with the short circuit ratings of the circuit breakers, of 65kA for 1 Seconds.

- Busbars shall be extensible at both ends, such extension shall entail the minimum possible disturbance to the existing busbar.

- Provision shall be made for locking busbar and circuit shutters separately in the Circuit Breaker compartment.

- Provision shall be made for integral circuit earthing and for busbar earthing. Means of earthing shall be by circuit breaker or purposely built earth switch. Mechanical interlocks to ensure correct switching operation shall then be provided.

- The earth switch shall be easy to operate by one operator and be spring loaded to ensure Effective Make Operation independent of the Operator Action. The earth switch shall be rated to make and carry for 3 seconds, the rated short-circuit current of the Air Circuit Breaker.

- The Status of the earth Switch shall be visible from the front of the Panel.

- The operation of the Earth Switch shall be set in such a way that during both the Close and Open Operations, a clearance of at least 9 inches shall be maintained between the operating handle and the bottom of the switchgear panel.

- It shall not be possible to insert the Earth switch Operating handle into Position except when the Circuit breaker is in the Test or Isolated Position.

- All earthing facilities shall be rated for fault making at the rated switchgear short- circuit current.

- The Panel wiring for protection, instruments, indication and metering circuits and other control accessories shall be completely done. All circuits for connection to external cables such DC & AC auxiliary supplies, external tripping, and Indications shall be wired up to the terminal Block at the Back of the panel where external cables shall be connected. At least 12 spare terminals shall be provided on the terminal board    for any future requirements.

- It is emphasized that Each Switchgear panel will have a terminal block at the back of the panel where all external cables such as Auxiliary DC supply, shall be made.

- Auxiliary 24V DC supplies for Circuit Breaker control, Alarm circuits and Protection relays, shall be controlled by suitably rated Miniature Circuit Breakers.

- The cubicle shall be tropical vermin proof. The plates shall be of mild steel thoroughly cleaned by shot blasting or other approved methods. They shall then be given a primary coat and two coats of contrasting colour of durable and weather resisting paint. The final coat shall be gloss and of Admiralty Grey (Shade 632) as specified in BS 381C. The final thickness of the paint shall not be less that 80 Microns at any point within the switchgear panel

- Anti-condensation heaters shall be provided inside each cubicle. They shall be located so as not to cause injury to personnel or damage to equipment. The heaters shall be controlled by a hygrostat with a variable humidity and temperature setting. The Heaters shall be dimensioned to ensure that condensation cannot occur within the switchgear panel.

- The 240V AC supply, for the heaters shall be controlled by a suitably rated single pole miniature circuit Breaker.

All the switchgear panels shall be rodent and vermin proof.

- Circuit Breakers

- The circuit breaker shall be three pole operated, indoor type, Air Circuit Breakers.

- The moving portion of each circuit breaker shall consist of a three-pole circuit breaker, operating mechanism, primary and secondary disconnecting devices, auxiliary switches, position indicators and necessary control wiring. The Auxiliary switches shall be of the plug-in type, with the male contacts mounted on the Breaker carriage and the female contacts on the plug-in cable connected to the Panel wiring. Other options may be considered where there is adequate proof that the auxiliary contacts will always be making firmly without mis-alignment. Finger contacts will however not be acceptable.

- The circuit breakers of the same current and voltage ratings shall be fully interchangeable, both electrically and mechanically.

- Name plate for the circuit breaker shall be provided with all the required details as per IEC Standards.

- The circuit breaker operating mechanism shall be motor wound spring operated, power closing with electrical release and with provision for hand charge.

- Mechanical indication shall be provided to indicate the state of the spring.

- The operating mechanism shall be completely trip free both mechanically and electrically.

- The circuit breaker shall have a mechanical operations counter

- One mechanical ON/OFF indicator, with inscription “ON” white letters on red background and inscription “OFF” white letters on green background shall be provided for the circuit breaker.

- One mechanical indication of the state of the spring inscription – SPRINGS CHARGED (white letters on red background); SPRINGS FREE, (white letters on green background) shall be provided for the circuit breaker.

- Where the Circuit Breaker is used for Circuit or Busbar Integral earthing, the control wiring of the breaker housing should be such that when the breaker is in circuit earth or busbar earth positions it shall only be operated mechanically and not electrically.

- The Circuit Breaker Maintenance and Operations Manual shall contain clear instructions on the Maintenance requirements of the Circuit Breaker (if any), to prevent Switchgear failure in service, due to excessive Fault Current Clearance or any other cause.

- Current Transformers

- Current transformers shall be Cast Resin Type and shall be accommodated inside the cubicle, in a separate compartment.

- The current transformers shall be in accordance with the requirement of IEC 60044- 1 and shall have the specified accuracy under load conditions and shall be able to withstand the effect of short-circuit fault current rating of the switchgear, of 65kA for 1 seconds.

- Current transformers shall have a rated burden as specified, sufficient for the connected Numerical Protection relays and Energy meters and instruments.

- Copies of Type Test certificates and routine Test Reports/Certificates as per IEC 60044-1, of CTs of similar Rating and Class as the specified CTs shall be submitted with the Tender for tender Evaluation Purposes. The Specified CTs must be within the Product Range of the manufacturer.

- Protection Relays

- The Measurement relays shall be Flush mounted and of Numeric Design, with event recording, Fault recording, power measurement, and shall be in accordance to IEC 60255.*

- Besides the communication port, the relays shall have a human – machine interface facility (MMI) with and LCD Screen where one can easily access relay information.

- Relay contacts shall be suitable for making and breaking the maximum currents, which they are required to control in normal service. Where contacts of the protective relays are not sufficient for Circuit Breaker Tripping, auxiliary Trip relays shall be provided, in order to prevent Damage to output contacts of the Measuring relay.

- Relay contacts shall make firmly without bounce and the relay mechanism shall not be affected by Panel vibration or external magnetic fields.

- Relays shall be provided with clearly inscribed labels describing their functions and IEC Device Function numbers.

- Relays shall be suitable for operation on the station D.C. supply without use of dropping resistors or diodes.

- To reduce the effect of electrolysis, relay coils operating on DC shall be so connected such that they are not continuously connected from the positive pole of the station battery.

- The relay Thermal rating shall be such that the fault clearance times on any

Combination of current and time multiplier settings shall not exceed the thermal withstand capability of the relay. (Max. fault current = 25kA).

- The relays shall be EMC 89/336/EEC compliant.

- Indications And Instruments

- All instruments shall be flush mounted and shall be in accordance with the requirement of IEC 51.

- Each cubicle shall have the following indications:-

- One indicator lamp to show the breaker in closed position - RED colour

- One indicator lamp to show the breaker in open position - GREEN colour

- The instruments shall be supplied as described under each panel in the subsequent sections.

- Power Cable Termination

Cable compartment design shall be suitable for heat shrinkable (or equivalent) jointing application termination. The compartment shall be adequate for connection of cables to evacuate the total load of 800 Amps.

- Accessories:

The following accessories shall be supplied with the switchboard at no extra cost:

| Spring charging handle | FOUR SETS |
| --- | --- |
| Circuit breaker draw out handle | FOUR SETS |
| Recommended set of circuit breaker maintenance tools | ONE SET |

- Ratings Of Switchgear and Equipment

- Incomer and Feeder Air Circuit Breaker

| Interrupting Medium | Air |
| --- | --- |
| Number of poles | 3 |
| Highest equipment Voltage | 600 V AC |
| Nominal System Voltage | 415 V AC |
| One minute power frequency withstand voltage | 3 kV |
| Impulse withstand voltage (BIL) | 8 kVp |
| Frequency | 50 Hz |
| Rated short time current | 50 kA |
| Rated Short circuit current withstand | 50 kA, 1 seconds |
| Auxiliary D.C. voltage for closing and tripping coils | 24 V DC |
| Auxiliary a.c. voltage | 240V AC, 50Hz |
| Tripping/closing coil auxiliary voltage | 24 V DC |
| Spring charging motor supply | 240 V AC |
| Rated normal Current | 800 A |

- Current Transformers for Incomer and Feeder Panels

|  | Rated Short time current (STC) withstand | 25 kA for 3 seconds |
| --- | --- | --- |
|  | Rated Voltage of the CT | 600 V |
|  | One minute power frequency withstand voltage | 3kV |
|  | Impulse withstand voltage | 8 kVp |
|  | Rated maximum continuous current | 800 Amps |

Ratio and class:

- Feeder Panels:

Core1:		C.T Ratio	: 800-400/1 A

Class		: 5P10

VA		: 10VA

Core2:		C.T Ratio	: 800-400/1 A

Class		: 0.5

VA		: 10VA

- Incomer panels:

Core1:		C.T Ratio	: 800-400/1 A

Class		: 5P10

VA		: 10VA

Core2:		C.T Ratio	: 800-400/1 A

Class		: 0.5

VA		: 10VA

- Tests

All switchgear shall be tested in accordance with the requirement of IEC 60298. Tests shall be carried out on the circuit breakers as per the requirement of IEC 60947. Current transformers shall be tested in accordance with the requirement of IEC 60044-1.

- Schedule of Tests to be carried out at the Manufacturer’s plant

- Test on Complete 415 V AC Switchgear Board

- Power frequency Withstand Test

- Megger Test

- Contact resistance test of Primary joints

- Power frequency Withstand Test on secondary Wiring

- Dimensional Checks

- Operational/Functional Tests

- Primary Injection Tests

- Calibration Tests on Relays and Instruments.

- 600 V AC Air Circuit Breaker

- Routine tests.

- Operation test.

- High Voltage test, dry. 3kV Power frequency Voltage test on controls and auxiliary circuits.

- Measurement of resistance of the main circuit.

- Type Tests: Submit copies of Type test Reports and Certificate

- Mechanical endurance test

- Temperature rise test.

- Impulse voltage test

- Interrupting Capacity test.

NB: Copies of Type Test Certificates for similar rated Circuit Breakers and Certified by National Standards and Testing Authority body or Reputable Third Party Test Laboratory shall be submitted with the Tender for Evaluation Purposes.

- Current Transformer

Type and routine tests shall be carried out at the manufacturer’s plant as per the requirement of IEC 60044-1, as listed below.

- Polarity Test and Verification of terminal markings

- Ratio and phase angle error test (accuracy class composite error test)

- Power frequency Tests on Primary and secondary windings

- Protection Relays, Controls And Measuring Devices

Requirements For 415 V Ac Switchgear Panels:

- General Requirements

Protection against electrical faults and abnormal conditions on 415 V AC Switchboard and the outgoing 11 kV feeders shall be conducted by the protective relays and associated switchgear. The Protection schemes shall be designed to ensure detection of all faults, fast discriminative fault clearance in order to ensure safety of personnel, equipment and continuity of Electric Power Supply.

- Bill Of Materials:

- Feeder Panels Requirements

Each Feeder Panel shall be equipped with the following Protection Relays, Measuring and indicating devices, Controls and other Accessories.

- Three phase overcurrent and earth fault.

- Combined Earth Fault and sensitive Earth Fault Relay.

- Three Ammeters with MDI with face plates available for both CT ratios. The Ammeter shall indicate both the instantaneous Load current and also the Maximum Demand Load current since the last reset.

- Energy Meter

- Voltmeter and Voltage Selector Switch, Circuit breaker control switch (Close, Open &Neutral), with a mechanical Lock, to prevent unintended tripping of the Circuit Breaker.

- Sensitive Earth Fault (SEF) mechanical isolation link or switch.

- Circuit Breaker ON(red) and OFF(green) Indication lamps.

- Door switch Operated Lighting point and Bulb.

- 3 Pin - Square Power Socket Outlet with red neon indicator.

- Suitably rated MCBs for Auxiliary 24V DC and for 240 V AC supplies.

- Common Alarm System

A common Alarm System shall be supplied equipped with the following:

- Urgent Alarm relay

- Non-urgent Alarm relay. NB: The urgent and non-urgent Alarm relays will be separate Relays.

- 16 window Annunciator relay.

- Hooter.

- Suitably rated MCBs for Auxiliary 24V DC and 240 V AC supplies.

- Incomer Panels Requirements

The Generator Panel shall be equipped with the following Protection Relays, Measuring and indicating devices, Controls and other Accessories:

- Three phase overcurrent and earth fault relay.

- Reverse Power Relay.

- Three Ammeter with MDI The Ammeter shall indicate both the instantaneous Load current and also the Maximum Demand Load current since the last reset.

- Energy Meter.

- Kilowatt Meter.

- Power Factor Meter.

- Voltage meter.

- Auto/Manual Selector Switch.

- Voltage selector switch.

- Circuit breaker control switch (Close, Open & Neutral) with mechanical locking to prevent un-intended operation.

- Circuit Breaker status ON(red) and OFF(green) Indication lamps.

- Door switch Operated Lighting point and Bulb.

- Pin - Square Power Socket Outlet with neon indicator.

- Suitably rated MCBs for Auxiliary 24V DC and 240 V supplies.

- Protection Relays And Control Devices

Reference Standards IEC 60255: Electrical Relays

- General Requirements

- The electrical Measuring protective relays shall be of Numeric Design. The Protective Relays and Auxiliary Relays shall operate successfully for any value of the DC supply voltage between 85% and 125% of the rated voltage of 24 V DC without exceeding the temperature rise limits for the operating coils.

- Each Measuring protection relay shall be of the Panel flush mounted, back connected, type with rectangular case. Each relay shall have a removable transparent cover or cover with a transparent window making the front of the relay visible. It is preferred that each measuring relay shall be of a withdrawable type from the front of the panel with sliding contacts, without opening the current transformer secondary circuits, disturbing external circuits or requiring disconnection of leads on the rear of the panels.

- Each protection relay shall be equipped with adequate electrically independent contacts, of adequate rating for Trip and alarm functions.

- Relays contacts shall be suitable for making and breaking the maximum currents, which they may be required to control in normal service. Where contacts of the protective relays are unable to deal directly with the tripping currents, Auxiliary Trip relays shall be provided. This will ensure safety for the protection relays output contacts.

- Relays contacts shall make firmly without bounce and the whole of the relay mechanism shall be as far as possible unaffected by vibration or external magnetic fields.

- Relays shall be provided with clearly inscribed labels on the surface of the panel describing their application in words e.g., “Three Overcurrent & Earth Fault Relay” in addition to the IEC numbering and outside.

- The Numerical Relays will be equipped with an RS232 Communication Port to facilitate connection to a Laptop. Also a communication port shall be provided on each Numerical Relay for Remote Interrogation and Programming of the Numerical Relays.

- The Relays will also have an MMI with LCD screen and Keypad to facilitate manual Relay programming and Data access.

- Relay Operation due to system fault, shall be indicated by a Red L.E.D. and the fault details (flags) shall be displayed on the MMI. Both the Relay Fault flags and Red L.E.D shall be reset via Reset push buttons without opening the Relay Cover.

- Detailed Specifications For Relays, Measuring And Indicating Instruments, Control Switches And Other Accessories

These specifications indicate the required performance characteristics for each of the Protection Relays and are in accordance with IEC 60255.

- Three phase over-current and earth fault relay

Should incorporate the following Features:

- Relay must be of Numerical Design.

- Shall be suitable for mounting on the panel front.

- Current setting range for overcurrent relay 0.2In-2.4In.

- Current setting range for earth fault relay 0.05In-0.8In.

- I.D.M.T characteristics according to BS142 or IEC255 i.e. SI, VI, EI, LTI, including definite time for the high-set Elements.

- Time setting multiplier 0.05 - 1.0.

- Broken conductor protection feature

- Highest Element for both overcurrent and earth fault with.

- Protection, with a setting range of 1-30In and a definite time delay setting of 0 - 60 Seconds.

- Drop off /pickup ratio >90%.

- Low transient overreach < 10%.

- LCD screen where the Settings and Measurement can be read.

- Keypad for manual programming of settings and data access Serial RS232 Port for Programming of the Relay and Access of Data using a Laptop Computer on the front surface of the Relay.

- Earth Fault Relay

Should incorporate the following Features:

- Relay must be of Numerical Type.

- Current setting range 0.05In-0.8In.

- I.D.M.T characteristics according to BS142 or IEC255 i.e. SI VI, EI, LTI, including definite time for the high-set Elements.

- Time setting multiplier 0.05 - 1.0.

- Highest Element with a setting range of 1-30In.

- Circuit Breaker Maintenance.

- Drop off /pickup ratio >90%.

- Low transient overreach < 10%.

- LCD screen where the Settings and Measurements can be read.

- Keypad for manual programming of settings and data access Serial RS232 Port for Programming of the Relay and Access of Data using Laptop Computer on the front surface of the Relay.

- Sensitive Earth Fault Relay

Should incorporate the following Features:

- Relay must be of Numerical Type.

- Current setting range for earth fault relay 0.010In- 0.8In.

- Definite time delay characteristic; setting range, 0- 30 Seconds.

- Drop off /pickup ratio >90%.

- Low transient overreach < 10%.

- LCD screen where the Settings and Measurements can be read.

- Keypad for manual programming of settings and data access.

- Serial RS232 Port for Programming of the Relay and Access of Data using a Laptop Computer on the front surface of the Relay.

- Reverse Power Relay

Should incorporate the following Features:

- Relay must be of Numerical design.

- Directional Power setting range, 0.2 to 20%.

- Definite time Delay; 0.4 to 10 seconds in suitable steps.

- LCD screen where the Settings and Measurements can be read.

- Keypad for manual programming of settings and data access Serial RS232 Port for Programming of the Relay and Access of data using a Laptop Computer on the front surface of the Relay.

- Annunciator Relay Unit

- Shall have Silence, Accept and Reset, push buttons, to control the Alarms.

- Shall be equipped with At Least 16 separate alarm Elements.

- Each of the elements shall be freely assigned to one of two common output.

- Alarms; Urgent and NON-urgent Alarm.

- Each Alarm Element shall have a Red L.E.D. to indicate ON status. It shall also have provision for fixing of Identification Label changeable on site. A flashing Alarm element shall be clearly visible.

- The Urgent and Non-Urgent common Alarms Shall be freely configurable to the output Relays.

- High Immunity against Electrical interference.

- Relay output for audible alarm and for self-supervision shall     be                                                                                                               provided.

- Integrated event register to provide analysis of the latest sixteen (16) events.

- Circuit breaker Close/Open control Switch

The switch shall have a mechanical interlock to prevent accidental operation of the switch. It shall have a close, Neutral and Open positions engraved on the switch. After an operation, the switch shall return to the neutral Position by spring Action.

- Indicating Instruments, Directly connected

ALL the instruments shall be of Moving Iron type

- The IP Protection Class shall be IP54.

- Accuracy class shall be 1.5, with maximum tolerated error of 1.5% of final scale value.

- Overload withstand shall be at least 20% continuous.

- All instruments shall be suitable for continuous operation under Tropical Climatic conditions.

- Ammeter Instrument with MDI– 800A

Indicating Range, 0 – 800 A for current input of 0 – 1A Full Scale Deflection, 800 A

Black Scale on white background Dimensions, 96X96 mm.

Shall have a resetable maximum demand indicator having a different color from the normal pointer as well as the normal instantaneous demand pointer.

Shall be Suitable for Flush Mounting on the panel.

- Voltmeter Instrument - 415 V AC

Indicating Range, 0 – 500 V AC Black Scale on white background Dimensions, 96X96 mm.

Suitable for Flush Mounting on the panel

- Signaling Hooter

The actuator system shall consist of a strong, non polarized electromagnet with an impact resistance sturdy casing.

Rated frequency 50 HZ.

Rated voltage shall be 240V AC; +6/-10 % Protection degree shall be IP 55

Operating mode continuous

Volume approximately 108 dB(A) 1 ¼ m Connection terminals shall be 2.5 mm 2

- Detailed Specifications For The Energy Meters

NB: These energy meters are for tariff metering similar to those used by Utilities

These specifications are for energy meters to be installed on the switchgear panels for purposes of Recording delivered Electrical Energy, and are in accordance with IEC 61334-4-4-1(DLMS Standard protocol).

The Energy Meter Supplied shall meet all the requirements detailed below:

The meters shall conform fully to IEC 687 for class 0.5S Energy Meters and any other relevant specifications.

The meters shall be programmable and relevant software and connection cable to laptop shall be provided. Meters complying with IEC 61334-4-4-1(DLMS Standard protocol) shall be preferred. The meters shall have memory and be capable of storage of at least 12 months load profile and other data.

The meters shall be capable of bi-directional metering so as to record faithfully, both export and import quantities. The accuracy shall be as per IEC 687 in both directions. The quantities to be displayed shall be determined by the user through use of Software that shall be provided. The meters shall be configurable for use in three phase 3/4-wire networks systems as follows:

3x240/415 V, 10 (100) A

3x240/415 V, /5 (1) A

3x /110V, /5 (1) A

The meters shall be usable on phase voltages of magnitudes ranging from 100V to 500V, 50 Hz. Meters with voltage-surge protection that meets IEC 687 specifications. The meters shall be for flush panel mounting. The meters shall have a non-volatile memory so as to ensure no loss of data during power failures. Security passwords and switches shall be provided to prevent unauthorized programming of the meter. The meters shall be fully year 2000 compliant and a certificate of confirmation shall accompany the tender.

The meters shall be suitable for operation in any part of the Republic of Kenya where the climate varies largely from temperatures between -5 and 40 Degrees Celsius and relative humidity reaching 95% in some parts. Operating altitudes ranging from sea level to 2200 meters above sea level. The meters shall support multi-tariff metering.

The Meters shall incorporate instrumentation for the following measurements: -

MW, MVAR, MVA, p.f., Phase Currents, Phase voltages and the angle between individual Phase Voltage and corresponding phase current. These measurements shall be visible on the Meter display.

The meters MUST have a capability of freezing billing readings on any selected date of the month.

The meters will measure maximum demand for MW, MVAR and MVA and these will be accessible on the Meter display. The Demand integration period will be programmable.

The CT and VT ratios shall be programmable. The meters shall have an accurate internal quartz controlled clock. It should be possible to reset the clock without loss of billing data. The supplier shall show proof of ISO 9000 and ISO 14000 standards compliance by attaching copies. The meters shall be provided with adequate sealing facilities to prevent tampering. The nameplate and meter details shall be clearly marked using materials and colors that are durable   and indelible.

In addition to requirements of IEC 687 the name-plate shall carry the following particulars:

- The inscription “ The property of REREC”

- Owner’s serial numbers as directed with a minimum 5mm figure height.

- Year of manufacture.

The meter base cover shall be of non-metallic, non-hygroscopic, flame retardant, polished material having high impact-resilience and low dirt absorption properties. The front cover may be of translucent material with a clear transparent front. The meter shall have a minimum of three sealing - provisions for the meter body, terminal cover and front cover (where applicable).

The meter terminal cover shall be the normal short length with provisions of easy bottom breakage for cable entry. The terminals shall be of bottom entry, and the arrangement shall be:

L1 L 1: L2 L2: L3 L3: N or

I1 V1 I1: I2 V2 I2: I3 V3 I3: N

The accuracy shall be Class 0.5. The meter errors shall comply with the requirement IEC 687 and shall be adjusted at the manufacturer’s works to be within between low and  high load and shall exhibit good stability. The meter shall have a warranty against any defects, which may develop due to faulty material, calibration, transportation or workmanship for a period of not less than eighteen months from the date of delivery. All defective meters shall be replaced at the supplier’s cost.

The following drawings and information shall be required with the  tender:

Meter drawing giving all the relevant dimensions. Wiring diagrams.

Description leaflet including details of programming of the meters User’s and service manuals.

- Schedule

The Tenderer shall after reading through the Technical Specifications and the Tender Documents in general complete the technical schedules below. The completed schedules shall accompany the bid.

ANNEX 2 – TECHNICAL REQUIREMENTS

| I | SWITCHGEAR PANEL |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREMENT | BIDDERS RESPONSE |
| 1 | Manufacturers name | State |  |
| 2 | Manufacturers letter of authorization | Provide copy |  |
| 3 | Copy of ISO 9001/2 certificate. | Provide copy |  |
| 4 | Type or designation number of Switchgear offered. | To provide |  |
| 5 | enclosure [IP] class of protection | IP42 |  |
| 6 | Rated voltage | 600 V |  |
| 7 | Rated power frequency withstand | 2kV |  |
| 8 | Rated lighting impulse withstand | 8 kVp |  |
| 9 | Metal clad compartments [CB, Busbar, LV, CT& Cable] attach layout drawing | 4 |  |
| 10 | Busbar material | Tinned copper |  |
| 11 | Dimensions [WxHxD [attach layout drawing] | Provide |  |
| 12 | Short circuit withstand | 25kV, 3 sec |  |
| 13 | Lockable door with viewing glass in CB compartments. | Yes |  |
| 14 | Shutters for Busbars [red] and circuit [yellow] provided. | Provide |  |
| 15 | Busbar rating | 800A |  |
| 16 | Circuit rating - Incomer | 800A |  |
| 17 | Circuit rating - Feeder | 800A |  |

| II | 600 V AC AIR CIRCUIT BREAKER |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREMENT | BIDDERS RESPONSE |
| 1 | Manufacturers’ name | State |  |
| 2 | Type or designation number of circuit breaker offered | Indicate |  |
| 3 | Name of manufacturer of vacuum interrupter | Provide |  |
| 4 | Rated circuit breaker voltage | 600 V |  |
| 5 | 1-minute power frequency withstand | 2kV |  |
| 6 | Impulse withstand voltage | 8kV |  |
| 7 | Rated short circuit current and withstand | 65kA, 1 sec |  |
| 8 | Auxiliary DC voltage for closing and tripping coils | 24 VDC |  |
| 9 | Auxiliary AC supply | 240 VAC |  |
| 10 | CB mechanism | Motor wound spring |  |
| 11 | Visible spring charged Mechanical indication on CB as per specifications. | Provide |  |
| 12 | Visible CB ON/OFF indications as per specifications | Provide |  |
| 13 | Connection of CB to auxiliary panel circuits via a plug-in cable | Yes |  |
| 14 | Operations counter | Provide |  |
| 15 | ACB Continuous Current Rating | 800 A |  |

| III | CURRENT TRANSFORMERS |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREM ENT | BIDDERS RESPONSE |
| 1 | Manufacturers name | Indicate |  |
| 2 | Type or designation number of CT | Indicate |  |
| 3 | Rated voltage of offered CT | 600 V |  |
| 4 | 1 minute power frequency withstand voltage | 2 kV |  |
| 5 | Impulse voltage withstand | 8 kVp |  |
| 6 | Short-circuit withstand current and duration | 65kA, 1 sec |  |
| 8 | Incomer Panel CT Details Ratio 800-400/1A Core 1: clx; VR>250V; Ie<0.02A Core 2: 15 VA, 5P10 Core 3: 15 VA cl 0.5 | Indicate Indicate Indicate Indicate |  |

| IV | PROTECTION RELAYS, AUXILIARY RELAYS AND CONTROL DEVICES: |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| [a] | THREE PHASE OVERCURRENT AND EARTH FAULT RELAY |  |  |  |  |
| ITEM | DESCRIPTION |  | REREC’S REQUIREM ENT |  | BIDDERS RESPONSE |
| I. | Manufacturers |  | State |  |  |
| II. | Type of designation name |  | State |  |  |
| III. | Design |  | Numeric |  |  |
| IV. | Flush mounting on panel |  | State |  |  |
| V | One time delayed element and two high set elements |  | Provide |  |  |
| VI. | MMI with keypad and screen |  | Provide |  |  |
| VII. | Software to be provided – |  | Provide |  |  |
| VIII. | 2 No. connection cable from relay to laptop computer to be provided |  | Provide |  |  |
| IX. | Serial RS232 port |  | Provide |  |  |
| [b] | EARTH FAULT RELAY |  |  |  |  |
| ITEM | DESCRIPTION | REREC’S REQUIREM ENT |  | BIDDERS RESPONSE |  |
| I. | Manufacturers name | Sate |  |  |  |
| II. | Type or designation name | State |  |  |  |
| III. | Design | Numeric |  |  |  |
| IV. | Flush mounting on panel | State |  |  |  |
| V | One time delayed element and two high set elements | Provide |  |  |  |
| VI. | Software to be provided – name | Provide |  |  |  |
| VII. | MMI with keypad and LCD screen | Provide |  |  |  |
| VIII. | Serial RS 232 port | Provide |  |  |  |

| [c] | SENSITIVE EARTH FAULT RELAY |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREM ENT | BIDDERS RESPONSE |
| I. | Manufacturers name | Sate |  |
| II. | Type or designation name | State |  |
| III. | Design | Numeric |  |
| IV. | Software to be provided – name | Provide |  |
| V | MMI with keypad and LCD screen | Provide |  |
| VI. | Serial RS 232 port | Provide |  |

| [d] | THREE-PHASE DIRECTIONAL POWER RELAY |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREM ENT | BIDDERS RESPONSE |
| I. | Manufacturers name | Sate |  |
| II. | Type or designation name | State |  |
| III. | Design | Numeric |  |
| IV. | Directional Power Setting Range | State |  |
| V | Flush mounting on panel | State |  |
| VI. | Definite time delay | Provide |  |
| VII. | Software to be provided – name | Provide |  |
| VIII. | MMI with keypad and LCD screen | Provide |  |
| IX. | Serial RS 232 port | Provide |  |

| [e] | ANNUNCIATOR RELAY UNIT |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREMENT | BIDDERS RESPONSE |
| I. | Manufacturers name | State |  |
| II. | Type or designation name | State |  |
| III. | Incorporates 16 Alarm elements | State |  |
| IV. | Has RED LED for visual indication | Provide |  |
| V | Has silence, accept and rest push buttons | Provide |  |
| VI. | Alarms freely assigned to urgent or non-urgent bus- wires | State |  |
| [f] | CIRCUIT BREAKER CLOSE/OPEN SWITCH |  |  |
| ITEM | DESCRIPTION | REREC’S REQUIREMENT | BIDDERS RESPONSE |
| I. | Manufacturers name | State |  |
| II. | Type or designation name | State |  |
| III. | Close and open position marked on the escutcheon plate | State |  |

| [g] | DIRECTLY CONNECTED INSTRUMENTS |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREM ENT | BIDDERS RESPONSE |
|  | 1 AMMETER WITH MDI- 800A |  |  |
| I. | Manufacturers name | State |  |
| II. | Type or designation name | State |  |
| III. | 96 mm x 96 mm | State |  |
| IV. | Flush panel mounting | State |  |
|  | 2. FREQUENCY METERS |  |  |
|  | Range | 45-55hz |  |
|  | Mounting | Flush in 48*96 sq.mm |  |
|  | 3. VOLTMETERs |  |  |
|  | Mounting | Flush |  |
|  | Size | 48 *96 sqm case |  |
|  | Frequency | 50Hz |  |
|  | Operating voltage | 415vac |  |
|  | Dielectric strength | 2kv rms for 1 min |  |

| [h] | MULTIFUNCTIONAL ELECTRICITY METER |  |  |
| --- | --- | --- | --- |
| ITEM | DESCRIPTION | REREC’S REQUIREMENT | BIDDERS RESPONSE |
|  | Class of accuracy | 0.5 |  |
|  | CT ratio | 800A-400/1A |  |
|  | Type or designation name | State |  |
|  | Mounting | Flush |  |
|  | Measuring Parameter | KWh,kVAh,kVAR Instantaneous P.F,KW,KVA, supply frequency,Phase voltage and Phase currents |  |
|  | Display | Customized backlit liquid crystal display |  |

PART III

| Lv Single Core Aluminium Cables (Pvc) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0. | Fore Word |  |  |  |  |  |  |  |  |
|  | 0.1 | This standard lays down specification for LV single core PVC insulated cables. |  |  |  |  |  |  |  |
|  | 0.2 | This specification is intended for procurement of materials and does not include provision of contract. |  |  |  |  |  |  |  |
|  | 0.3 | This specification is based on IEC 502 and BS 6346. It is subject to revision as and when required. |  |  |  |  |  |  |  |
|  | 0.4 | This specification supersedes all specifications for LV single core PVC insulated cables issued before the revision date. |  |  |  |  |  |  |  |
| 1. | Scope |  |  |  |  |  |  |  |  |
|  | 1.1 | This specification is for single core, stranded aluminium conductors, polyvinyl chloride (PVC) insulated, armoured, PVC outer sheathed power cables for operation up to and including 600 volts to sheath and 1000 volts between conductors. |  |  |  |  |  |  |  |
|  | 1.2 | This specification is for following cable sizes: |  |  |  |  |  |  |  |
|  |  | 630 sq. mm Aluminium conductor PVC insulated single core cable. |  |  |  |  |  |  |  |
|  |  | 300 sq. mm copper conductor PVC insulated single core cable. |  |  |  |  |  |  |  |
| 2.0 | Materials And Construction |  |  |  |  |  |  |  |  |
|  | 2.1 |  | The cable shall be made from circular stranded compact plain aluminium conductor as per IEC 228. |  |  |  |  |  |  |
|  | 2.2 |  | The insulation shall be polyvinyl chloride (PVC) complying with the requirement of IEC 502 for type PVC/A. |  |  |  |  |  |  |
|  | 2.3 |  | The insulation shall be applied by extrusion process and shall form a compact homogeneous body. The insulation shall concentrically cover the conductor |  |  |  |  |  |  |
|  | 2.4 |  | Extruded over-sheath shall be of black polyvinyl chloride (PVC). |  |  |  |  |  |  |
|  | 2.5 |  | The cable shall be clearly and permanently embossed with the following information throughout the length of the over-sheath. Letters and figures raised and consist of upright block characters. Minimum size of characters not less than 15% of average overall cable diameter. |  |  |  |  |  |  |
|  |  |  | 600/1000 VOLTS PVC CABLE |  |  |  |  |  |  |
|  |  |  | Year of manufacture |  |  |  |  |  |  |
|  |  |  | (Example: ‘600/1000 VOLTS PVC CABLE 1996’) |  |  |  |  |  |  |
| 3.0 | Standard Sizes And Characteristics |  |  |  |  |  |  |  |  |
|  | 3.1 |  | The characteristics of the cables shall comply with the following table |  |  |  |  |  |  |
|  |  |  | Item |  |  | Characteristics |  |  |  |
|  |  |  | Conductor resistance |  |  | Not more thank the value indicated |  |  |  |
|  |  |  | A.C. withstand voltage |  |  | To withstand the indicated value for 5 min. |  |  |  |
|  |  |  | Insulation resistance |  |  | Not less than the value indicated. |  |  |  |
|  |  |  | Tensile strength |  | PVC | Tensile strength, minimum |  | 12.5N/mm (1.27 Kg/mm) |  |
|  |  |  | Ageing requirement* |  | PVC | Elongation, Minimum percentage of unaged value |  | 150% 75 - 125% |  |
|  | * Treatment: PVC temperature 100 - 20°c duration 168 hrs |  |  |  |  |  |  |  |  |
|  | 3.2 |  | The cable shall conform with the following requirements |  |  |  |  |  |  |
|  |  |  | Cable size |  |  |  | 630 sq. mm |  | 300 sq. mm |
|  |  |  | Nominal sectional area |  |  |  | 630 sq. mm |  | 300 sq. mm |
|  |  |  | Thickness of insulation |  |  |  | 2.8 mm |  | 2.4 mm |
|  |  |  | Thickness of outer sheath |  |  |  | 2.2 mm |  | 2.2 mm |
|  |  |  | Nominal overall diameter |  |  |  | 38.8mm |  | 28.0 mm |
|  |  |  | Approximate net weight |  |  |  | 6200 kg/km |  | 3100 kg/km |
|  |  |  | Test voltage |  |  |  | 3kV/5min |  | 3kV/5min |
|  |  |  | Maximum conductive resistance |  |  |  | 0.007 ohms/km |  | 0.0120 ohms/km |
| 4.0 | Tests |  |  |  |  |  |  |  |  |
|  | 4.1 |  | The cable core, sheath and completed cable shall be tested in accordance with the requirements of BS 6346. |  |  |  |  |  |  |
| 5.0 | Packing |  |  |  |  |  |  |  |  |
|  | 5.1 |  | The cable shall be wound on wooden drums such as to prevent damage during transportation. The wooden drums shall be made from treated timber resistant to termite attack. |  |  |  |  |  |  |
|  | 5.2 |  | The following description shall be marked on one flange of the reel |  |  |  |  |  |  |
|  |  |  | (a) | Direction of rotation of the reel |  |  |  |  |  |
|  |  |  | (b) | Type of cable |  |  |  |  |  |
|  |  |  | (c) | Number of conductors and size |  |  |  |  |  |
|  |  |  | (d) | Length |  |  |  |  |  |
|  |  |  | (e) | Net weight and gross weight |  |  |  |  |  |
|  |  |  | (f) | Manufacturer’s name |  |  |  |  |  |
|  |  |  | (g) | Year of manufacture |  |  |  |  |  |
| 6.0 | References |  |  |  |  |  |  |  |  |
|  | 6.1 |  | The following documents were referred to during the preparation of this specification. In cases of conflict, the provisions of this specification shall take precedence. |  |  |  |  |  |  |
|  |  |  | Unless otherwise specified, the latest revision, edition and amendments shall apply |  |  |  |  |  |  |
|  |  |  | IEC 502:(1983): Extruded solid dielectric insulated power cables for rated voltages from 1 kV up to 30 kV. |  |  |  |  |  |  |
|  |  |  | IEC 228(1978): Conductors of insulated cables. |  |  |  |  |  |  |
|  |  |  | BS 6346 PVC insulated cables for electricity supply |  |  |  |  |  |  |

PART IV

Specifications for 0.415/11kV Step-up Transformer

FOREWORD

This specification has lays down requirements for 0.415/11 kV Step-up Transformer. It is intended for use in purchasing the transformers.

It shall be the responsibility of the manufacturer to ensure adequacy of the design and good engineering practice in the manufacture of the 0.415/11kV Step-up Transformer for REREC. The manufacturer shall submit information, which confirms satisfactory service experience with products, which fall within the scope of this specification.

It is expected that manufacturers will provide energy efficient standard design that will provide high level of efficiency and significant initial cost saving.

- SCOPE

This specification is for oil-immersed, air-cooled, outdoor type three phase 0.415/11 Kv Step-up Transformer for ac system operated at 50 Hz.

The transformers shall be connected to an off-grid power station to step-up generation output of 415V to 11 kV distribution network.

- REFERENCES

The following documents were referred to during the preparation of this specification; in case of conflict, the requirements of this specification shall take precedence.

IEC 60076:	Power Transformers

BS 381C:	Specification for colours for identification, coding and special purposes

IEC 60296:	Specification for unused mineral insulating oil for transformers and switchgear

IEC 60354:	Loading guide for oil – immersed power transformers.

BS 6436:	Specification for Ground Mounted Distribution

Transformers for Cable Box or Unit Substation Connection.

- TERMS AND DEFINITIONS

For the purpose of this specification the definitions given in the reference standards shall apply.

- REQUIREMENTS

- SERVICE CONDITIONS

- Operating conditions

- The transformers shall be suitable for continuous operation outdoors in tropical areas at altitudes of up to 1500m above sea level, humidity of up to90%, average  ambient temperature of +30ºC with a minimum of -1ºC and a maximum of +40ºC and heavy saline conditions along the coast.

- System characteristics

- The primary shall be 415V, 50Hz while the secondary shall be 11 000V, 50Hz, three wire (the neutral solidly earthed).

- The 11kV overhead system is of unearthed construction (i.e. without aerial earth wire).

- DESIGN AND CONSTRUCTION

- General

- The transformer shall be three phase, oil immersed type, air cooled, core type, outdoor and shall be designed, manufactured and tested as per IEC 60076 and this specification.

- The transformer shall be free breathing type provided with a conservator and a dehydrating breather (cobalt free). The conservator shall be in such a position as not to obstruct the electrical connections to the transformer and shall have oil gauge at one end marked with oil levels. The conservator shall have a feed valve.

- The complete transformer shall be painted and protected against corrosion, and the final colour of the exterior surface shall be Dark Admiralty Grey colour No. 632 as per BS 381C. The inside of the tank shall be coated with oil resisting varnish or paint so that oil cannot come into contact with tank or metal at any point.

- Each transformer shall be suitable for ground mounting (on a plinth).

- Drawings and documentation for the transformer offered shall be given, clearly detailing important dimensions, clearances, accessories, fittings, internal assembly, material details and any special features of the offered design.

- Tank

- The transformer tank shall be constructed of mild steel plates. Tank thickness shall be stated in the Technical Particulars

- The transformer tank shall be sealed by means of suitable gasket and be fitted with earthing terminals. Eight(8No.)non-standard shearing bolts to deter unauthorised opening shall be used on bolted corners and centres of sides of the top cover. Relevant tools for unbolting the transformer shall be delivered with the transformer.

- Core

- The cores shall be constructed of high quality low loss grain oriented electrical steel laminations. The design shall ensure no hot sections due to over fluxing or circulating currents across the laminations. The flux density at any point shall not exceed 1.65 Tesla.

- The cores shall be clamped effectively with metal cross-arms and be fitted with core lifting lugs. The manufacturer shall demonstrate experimentally or via a previous test report, that the whole structural frame-work supporting the transformer windings and the core can definitely withstand repeated transformer short-circuits.

- Windings

- The windings shall be of electrolytic copper capable of sustaining short circuit forces on the transformer.

- The primary windings shall be of full coil copper wires as opposed to segmented winding and the secondary windings shall be coil or foil of copper.

- The HV and LV windings shall be separated so as to allow for cooling and ease of repair. Insulating sleeves for the transformer tappings shall be in crepe paper or better.

- Tapping

- The secondary winding (11 kV) shall have tappings at  2 X 2.5% operated by an off-circuit self-positioning tapping switch with marked position indicators. Tapping details shall be included on the transformer name plate.

- Switch position No. 1 shall correspond to maximum plus tapping. The make contacts of the tap changer shall be robust and of sufficient surface area.

- Vector Group

- The three-phase transformer shall be wound to IEC vector reference YNd11.

- The star point of the secondary winding shall be brought out to a neutral bushing.

- Cable Boxes, Bushings and Clearances

- The transformer shall be fitted with cable box on the primary side (LV) and have open bushings on the secondary side (11 kV).

The LV cable box shall be unfilled type and suitable for terminating up to 7No. single core PVC cables of 240 mm2 on a clamp pad, cables entry from bottom.

- The 11 kV bushings shall be open and shall have outdoor brown glazed weather proof bushings provided with external stud for conductor sizes from 7.8 mm to 18.2 mm diameter mounted on the tank top cover.

- Clamp connector shall be provided on each bushing.

- The bushings shall be constructed, arranged and fitted in such a manner as to be changed without opening the transformer.

- Each bushing shall be fitted with adjustable double-gap arcing horns set at 2 X 25mm gaps.

- The minimum external electrical clearances and minimum creepage distances of the 11 kV bushings shall be as indicated below:

| Nominal System Voltage between Phases |  | 11 kV |
| --- | --- | --- |
| Minimum clearances between phase to earth | mm | 250 |
| Minimum Clearances between phases | mm | 300 |
| Creepage distance | mm | 300 |

- Oil and Cooling

- Cooling of the transformer shall be by natural circulation of oil and natural circulation of air (ONAN). Loading will be as per IEC 60354.

- Each transformer shall be dispatched filled with oil to the correct level and ready for service. The oil shall be new (unused), uninhibited mineral insulating oil class I as per IEC 296. The oil shall be PCB-free.

- Fittings and Accessories

- No drain valve shall be fitted.

- Oil gauge shall be provided on each transformer and shall be of dial or floater type. The oil gauge shall be clearly readable by an operator standing at a distance of 5 meters away from the transformer. The maximum and minimum oil level marks shall fall within 50% of the full range of the gauge with the nominal oil level being at the center of the range.

- Each transformer shall be complete with an oil temperature thermometer in a visible and secure position.

- Each transformer shall be complete with a pressure relief device fitted in a visible and secure position. No part of the pressure relief device shall extend to a height greater than the HV bushings.

- Rating

- The transformer shall be capable of carrying its full normal rated current continuously under the tropical conditions stated (maximum ambient temperature of 40C) and at any tapings without the temperature rise in the hottest region exceeding 55C and 60C in oil and winding respectively. Documents to support this shall accompany the tender.

- The transformer shall be capable of sustaining a three-phase symmetrical short circuit on the secondary side with power maintained on the primary side without damage or distress for 2 seconds.

- The rated withstand voltages for the transformers shall be as follows:

|  | Rated short duration power frequency withstand voltage (r.m.s.) |
| --- | --- |
| 0.415/11 kV Transformer | 38kV |

- Impedance Voltage

- The impedance voltage measured at the principal tap shall not exceed 5.0%.

- Losses and Capitalisation

- The guaranteed transformer losses, measured at full load operation, unity power factor and rated voltage shall be submitted with the tender. The loss measurements (no-load and full-load) shall be adjusted to 75 degree Celsius and submitted for evaluation.

- TESTS AND INSPECTION

- Type tests and routine tests shall be done in accordance with the requirement of IEC 60076 and this specification. It shall be the responsibility of the manufacture to perform or to have performed all the tests specified.

- Certified true copies of previous type test reports by the relevant International or National Testing/Standards Authority of the country of manufacture (or ISO/IEC 17025 accredited laboratory) shall be submitted with the offer for evaluation (all in English Language). A copy of accreditation certificate for the laboratory shall also be submitted.

- Routine test reports for the transformer to be supplied shall be submitted to REA for approval before shipment/delivery. REA shall witness routine tests as well as impulse withstand voltage and temperature rise tests at the factory before dispatch.

- MARKING AND LABELLING

- Each transformer shall be provided with a rating plate of weatherproof material, fitted in a visible position, showing the appropriate details listed in IEC 76. The entries on the plate shall be indelibly marked (either by etching, engraving or stamping).

- In addition, the name plate shall include load and no load losses for the highest, lowest and principle tap positions, temperature class of insulation, connection diagram and the inscription 'PROPERTY OF RURAL ELECTRIFICATION AND RENEWABLE ENERGY CORPORATION all marked indelibly as in 6.1

ANNEX C: TECHNICAL REQUIREMENTS FOR STEP-UP TRANSFORMER

| Item | Description |  | REREC’S REQUIREMENT | BIDDER’S RESPONSE |
| --- | --- | --- | --- | --- |
| 1 | Quantity |  | 1 |  |
| 2 | Transformer Rating | kVA | 315KVA |  |
| 3 | System Frequency | Hz | 50 |  |
| 4 | Transformer external paint |  | Dark Admiralty Grey colour No. 632 as per BS 381C |  |
| 5 | Corrosive environment |  | High |  |
| 6 | Dimensions overall height overall length overall width Total mass | mm mm mm kg | State State State State |  |
| 7 | Tank type |  | Breathing |  |
| 8 | Tank sealing; |  | Bolted |  |
| 9 | Under-base; |  | Flat |  |
| 10 | Skids and Jacking lugs for concrete plinth mounting |  | 40 mm diameter axle holes |  |
| 11 | Details of jacking pads |  | State |  |
| 12 | Lifting lags for cover for tank for core |  | To provide To provide To provide |  |
| 13 | Terminations |  | Cable box |  |
| 14 | Position of bushings |  | 11kV: Top, LV: Cable Box |  |
| 15 | Medium-voltage bushings colour material creepage distance phase to earth clearance phase to phase clearance Low-voltage bushings material/colour creepage distance phase to earth clearance phase to phase clearance Terminal: stem & nuts or clamp | mm mm mm mm mm mm | Brown Porcelain 25 mm/kV Specify Specify Brown Porcelain 25 mm/kV Specify Specify Clamp pad |  |
| 16 | Cooling method |  | ONAN |  |
| 17 | Core type |  | Laminated stackings |  |
| 18 | Core clamping |  | Specify |  |
| 19 | HV Winding |  | Full coils of electrolytic copper |  |
| 20 | LV Winding |  | Electrolytic copper coils or copper foils |  |
| 21 | Primary voltage Secondary voltage Number of phases; | V V | 415 11000 Three phase |  |
| 22 | Rating of neutral terminal |  | As phase terminal |  |
| 23 | Tap Changer |  | NLTC, 2X2.5% Tapping range |  |
| 24 | Vector symbol |  | YNd11 |  |
| 25 | Losses corrected to 75°C no-load losses full load cu losses full load total losses Transformer efficiency at unity power factor, rated voltage and full load (75°C) | W W W % | Specify Specify Specify Specify |  |
| 26 | Impedance voltage maximum tap nominal tap minimum tap | % % % | Specify Specify Specify |  |
| 27 | Insulation level medium-voltage low-voltage | kV kV | 38 3 |  |
| 28 | BIL Tests (IEC 60076) |  | To be done at 38kV during factory visit (clause 5.3) |  |
| 29 | Temperature Rise Test (IEC 60076) |  | To be done during factory visit (clause 5.3) |  |
| 30 | Routine Tests (IEC 60076) |  | To be done during factory visit (clause 5.3) |  |
| 31 | Transformer Leakage Test |  | To be done during factory visit (clause 5.3) |  |
| 32 | Tank Thickness |  | Specify (Not less than 6.40mm) |  |
| 33 | Transformer Bachholz Relay fitting |  | To provide |  |
| 34 | Transformer pressure relief valve |  | To provide |  |
| 35 | Temperature gauge |  | To provide |  |
| 36 | LV termination Box |  | To provide |  |

PART V

## Specification for 11 KV Circuit Breakers (Triple Pole)

FOREWORD

The specification is intended for use in procurement of the Circuit Breaker from manufacturers. The specification is based on IEC 56 and BS5311 and is subject to revision as and when required.

It shall be the responsibility of the manufacturer to ensure adequacy of the design and good engineering Practices in the manufacture of the 11 KV Circuit Breaker. The manufacturer shall submit information, which confirms satisfactory service experience with products, which fall within the scope of this specification.

- SCOPE

This specification covers design, engineering, manufacture, testing, inspection before dispatch packing, forwarding, transportation, insurance during transit, delivery to site of 11 KV Outdoor Vacuum Circuit Breakers together with controls, auxiliary equipment and support structure for use in 0.415/11KV substation, off grid Solar plant.

The specification is for triple pole operated circuit breaker.

- REFERENCES

The following documents were referred to during the preparation of this specification; in case of conflict, the requirements of this specification shall take precedence.

IEC 60056:	High Voltage alternating current circuit breakers.

IEC 2300:	Designed and manufacturing of VCB.

IEC 144:	Degree of protection of enclosures for low voltage switch gear and control gear.

BS 5311:	Specification for A.C. circuit breakers of rated voltage above 1 kV.

This particular standard or recommendation in this specification does not relieve the Supplier of the necessity of providing the goods and services complying with other relevant standards or recommendation

- TERMS AND DEFINITIONS

For the purpose of this specification the definitions given in the references mentioned in clause 2 shall apply.

- REQUIREMENTS

  - SERVICE CONDITIONS

    - Operating conditions

      - The circuit breaker shall be suitable for continuous outdoor operation in tropical areas  with the following atmospheric characteristics:

        - Altitude: 2200m above means sea level

        - Pollution: Heavy saline atmosphere

        - Humidity: Up to 90%

        - Ambient temperatures of +30o C average, (+45o C Max. and -1o C Min.)

        - Isokeramic level: Up to 180 thunderstorm days.

    - The circuit breaker shall be connected to an overhead system which is generally unearthed (without aerial earth wire).

    - The circuit breakers shall be suitable for 3 phase 50Hz solidly grounded neutral system and shall have normal current carrying capacity and symmetrical short circuit current breaking capability as mentioned hereunder.

  - CONSTRUCTION

    - The circuit breakers shall be structure mounted open type with vacuum as interrupting media incorporating interrupter. There shall be a common drive mechanism actuating the interrupter, which must work in synchronism. These breaker shall be provided with suitable local control while provision shall be made for remote control.

    - The circuit breakers shall be three pole operated, out-door type, Vacuum insulated and     shall comply with the requirements of IEC 60056 and/or BS 5311.

    - The circuit breakers shall be fitted with spring mechanism. The inherent design of these circuit breakers shall be such that they shall satisfactorily perform all test duties and interrupt out-of- phase current and produce very low over voltage (<2.0p.u.) on all switching circuits, capacitive and inductive to IEC:56, IS:13118 and other associated standards mentioned in the clause of this specification.

    - All the three poles shall be interconnected by a suitable shaft, linked to the operating mechanism so that poles are operated simultaneously with common gas pressure monitor.

    - All the three poles of circuit breaker shall be operated by local electrical from the mechanism in the housing and remote electrical from remote panel.

    - The mechanism box shall have a mechanical facility for manually operating the three           poles.

    - Insulation creepage distance shall not be less than 25mm per kV of maximum operating voltage between phases.

  - OPERATING MECHNANISM

    - (a) The operating mechanism shall be suitable for mounting at the circuit breaker supporting structure, and below the circuit breaker in a weather-proof, dust- proof, vermin-proof and well-ventilated housing.

- The degree of protection shall be class IP 54 as per the requirement of IEC 144.

- The housing shall be provided with padlocking facility.

    - Operating mechanism shall be trip free during the entire closing sequence.

    - (a) Operating mechanism shall be provided with motor wound spring charging mechanism with provision for hand operated manual charging. Pressure actuated    mechanism shall not be accepted.

- The Motor shall be universal with operating voltage of either 110 Volts d.c or 110 Volts a.c.

    - A set of at least five normally closed and five normally open spare potential free contacts shall be provided for remote electrical indication as well as electrical interlocking and shall be wired to a terminal block in the housing.

    - A minimum of twenty (20) spare terminals shall be provided for connection to the current and voltage transformers.

      - Sixteen (16) of these spare terminals shall be specifically used for current transformers and shall be capable of carrying 10Amps continuously and have facilities for shorting terminals.

      - Four (4) of these terminals shall be used for the voltage transformer and shall have facilities for isolation.

    - The circuit breaker shall be provided with Local/Remote selector switch. The selection of the local operation shall inhibit the operation of the circuit breaker from   any remote source.

    - The circuit breaker shall be provided with a local switch for Open/Neutral/Close operation.

    - The breaker shall normally be operated by remote electrical control with electrical tripping by shunt trip coil. Provision shall be made for local electrical operation and mechanical operation. The following facilities shall be provided in the circuit breaker local control cabinet:

- LOCAL/ REMOTE selector switch of stay put type. The selection of ‘local’ operation shall inhibit the operation of the breaker from any remote source.

- ON/NEUTRAL/ OFF control switch or ON and OFF push buttons. The push buttons shall be momentary contract type with rear terminal connections. The close push button shall be of green colour and the open push button red colour.

- MECHANICAL EMERGENCY TRIP DEVICE: suitable for manual operation in the event of failure of electrical supplies. The device shall be accessible without opening any access doors and distinctly labelled. It shall be shrouded and protected against inadvertent operation.

- Means shall be provided for manual operation of these circuit breakers during failure of auxiliary power in addition to electrical operation.

- Means shall be provided to prevent the mechanism from responding to a close signal when the trip coil is energized or to reclosing from a sustained close signal either opening due to a trip signal or failure to hold in the closed position.

- The circuit breaker shall be able to perform 10,000 operating cycles at no load in accordance with IEC: 17A/474/CD for circuit breakers for auto reclosing duties.

    - Mechanically operated indication to show the status of the circuit breaker operations (open/close and springs charged/discharged) shall be provided.

    - A mechanically operated circuit breaker position indicator of non-corroding material shall be provided in a location visible from the operating side of the breaker without the necessity to open the mechanism door. The word ‘OFF’ in white letter on green background shall be used to indicate that the breaker is in the opening position and the word ‘ON’ in white letters on a red background to indicate that the breaker is in the closed position. The drive for the device shall be positive in both directions and provision shall be made for local and remote electrical indication.

    - Indication of spring charging condition shall be provided as mentioned in this specification. Mechanical counters to record the number of closing operations shall be provided for circuit breaker mechanism.

    - The circuit breaker shall be provided with suitable terminals for connecting 3” (outside diameter) tinned copper tubes.

    - The circuit breaker shall be provided with means to prevent contact pumping should                                              the circuit be energized while tripping command is issued.

4.1.12 Mechanical interlock arrangement shall be provided on the mechanism such that it  shall not be possible to withdraw the interlock with circuit breaker in closed position.

- RATINGS

|  | Description | Rating |
| --- | --- | --- |
| 1 | Nominal Voltage | 11 kV |
| 2 | Highest Voltage | 12 kV |
| 3 | Frequency | 50 Hz |
| 4 | Normal Current | 630 Amps |
| 5 | Rated short circuit Current | 21KAmps |
| 6 | Duration of short circuit | 3 Sec. |
| 7 | First pole to clear factor | 1.5 |
| 8 | Transient recovery voltage peak value | 62 kV |
| 9 | Operating sequence | 0-0.3 sec – CO – 3min – CO |
| 10 | Auxiliary D.C Voltage for closing & tripping coils | 110 V d.c. |
| 11 | Motor charging supply | 110 V d.c. |
| 12 | Auxiliary A.C. Voltage | 415/240 V, 50 Hz |
| 13 | Impulse withstand voltage | 75 kV peak |
| 14 | One minute power frequency withstand voltage | 28 kV r.m.s. |
| 15 | Creepage distance of insulator | 350 mm |
| 16 | Minimum clearance between phases | 250 mm |
| 17 | Minimum clearance to earth | 300 mm |

- CONTROL AND RELAY PANEL

  - The bidder to design and Manufacture control and relay panel for remote operation of the outdoor 11KV circuit breaker, it will be used for control and monitoring of Circuit breaker.

  - The control and relay panel shall be complete with all main and auxiliary relays, annunciation relays, fuses, links, switches, wiring, lebels, terminal, blocks, bolts, illumination, cable, glands etc.

  - The indoor control panel for outdoor VCB should be equipped with the following:

- IDMT Numerical relay

- Master trip relay

- Trip Circuit Supervision relay.

- Indication

- Voltmeter

- Ammeter

- Switches

- DRAWING AND MANUALS

  - Two sets of operational manuals and drawings detailing dimensions, panel layout, wiring and schematic shall be provided.

- PACKING

  - The circuit breaker and associated components shall be packed in a manner as to protect it from any damage in transportation and repeated handling.

  - Each assembly and package of items associated with the circuit breaker shall be suitably marked.

  - Where an item includes a number of components to form a complete assembly, all components shall be included in one composite package which shall be firmly strapped and bound together.

- TESTS

  - The manufacturer shall be responsible for performing or for having performed all the required tests specified in this specification. Tenderers shall confirm the manufacturer’s capabilities in this regard when submitting tenders. Any limitation shall be clearly specified.

  - Tender documents shall be accompanied by copies of Type test and Routine rest reports and certificates for similar rated equipment for the purpose of tender evaluation. Type test reports and certificates shall be certified by the National Standards and Testing Authority (NSTA) of the country of origin. Where a body other than NSTA is used to certify the type-test reports, a copy of the certificate of accreditation shall be attached. Current contact information of the testing and certification Authority shall be provided. Tenderers should note that this requirement is mandatory.

  - Upon completion of the manufacturing process, routine tests shall be carried out as per IEC 60056. In addition to these tests, Impulse and short circuit breaking tests shall            be carried out on a sample of the circuit breakers and the results endorsed by the NSTA of the country of manufacture.

  - Routine test reports shall be completed for breaker and made available before the inspection by REREC representatives.

  - All circuit breakers shall be subjected to inspection by two REREC Engineers or her representative at place of manufacture and all routine tests on randomly picked breakers carried out in their presence. REREC representatives shall approve shipment of the equipment if they are satisfied that the requirements of the specification are fully met. The supplier shall quote separately for this inspection. The full cost of the visit, including air tickets shall however be borne by the supplier of the equipment.

  - A detailed list and contract addresses of previous customers shall be submitted with the tender. The manufacturer shall indicate a monthly and annual production capacity and experience in the production of the type and size of circuit breaker he is offering. List of workshop tools and equipment shall also be appended.

- INFORMATION

  - Draft design and construction drawings shall be submitted to REREC before the manufacturing of breakers commence. REREC undertake to submit their comments or approval for the drawings within three weeks of receiving the draft copies.

  - Sufficient relevant technical details and drawings shall be submitted for the purpose of Tender Evaluation. Tenders which do not meet this requirement shall be considered non-responsive.

  - Before manufacturing commences, REREC engineers or her Agents will need to inspect the manufacturing facility at no extra cost to REA, excepting the cost of their transportation to the nearest major airport in the country. Such inspection shall not in any way prejudice the purchaser’s rights and privileges throughout.

  - Manufacturers shall indicate any additional measure taken to mitigate electrical and mechanical stress resulting from system surges.

ANNEX D: TECHNICAL REQUIREMENTS FOR:

- 11kV CIRCUIT BREAKER

| Item | Particulars | RERE’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Service type | Outdoor |  |
|  | No of Poles | 3 |  |
|  | Interrupting Medium | Vacuum |  |
|  | Nominal Voltage | 11 kV |  |
|  | Highest Voltage | 12 kV |  |
|  | Frequency | 50 Hz |  |
|  | Normal Current | 630 Amps |  |
|  | Rated short circuit Current | 21KAmps |  |
|  | Duration of short circuit | 3 Sec. |  |
|  | First pole to clear factor | 1.5 |  |
|  | Transient recovery voltage peak value | 62 kV |  |
|  | Operating sequence | 0-0.3 sec – CO – 3min – CO |  |
|  | Auxiliary D.C Voltage for closing & tripping coils | 110 V d.c. |  |
|  | Motor charging supply | 110 V d.c. |  |
|  | Auxiliary A.C. Voltage | 415/240 V, 50 Hz |  |
|  | Impulse withstand voltage | 75 kV peak |  |
|  | One minute power frequency withstand voltage | 28 kV r.m.s. |  |
|  | Creepage distance of insulator | 350 mm |  |
|  | Minimum clearance between phases | 250 mm |  |
|  | Minimum clearance to earth | 300 mm |  |
|  | Auxiliary switch | At least 5No + 5NC |  |
|  | Degree of Protection | IP54 |  |
|  | Applicable Standards | IEC62271-100,IS13118 |  |
|  | Warrant | 2 year |  |

- NEUTRAL CURRENTTRANSFORMERS; RATIO 50-25/1, 0.2S CLASS

| Item No. | Particulars | RERE’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer’s name & address | State |  |
|  | Model | State |  |
|  | Type. | Outdoor, Oil-Immersed live tank effectively earthed neutral Current transformers |  |
|  | Warranty | 3 Years |  |
|  | Rated Voltage/Highest Voltage. | 11KV/12KV |  |
|  | Frequency | 50HZ |  |
|  | Rated primary Current. | 50A and 25A |  |
|  | (i) Core 1 | 50-25A |  |
|  | (ii) Core 2 | 50-25A |  |
|  | Secondary Core details. |  |  |
|  | (a) Number of Cores. | 2 |  |
|  | (b) Rated secondary current. | 1A |  |
|  | (i) Core 1 | 1A |  |
|  | (ii) Core 2 | 1A |  |
|  | (c ) Rated output/Burden | 5VA |  |
|  | (d) Class of accuracy | 0.2S |  |
|  | (e ) Accuracy limit factor. | <5 |  |
|  | Turns Ratio. | 50/1A and 25/1A |  |
|  | Short time thermal current & its duration | 12.5 KA/ 1 Sec |  |
|  | - Rated continuous thermal current. - Temperature rise over ambient. | 1.2 times continuous 45 deg C, as per IS 2705 |  |
|  | One minute power frequency dry and wet withstand voltage on primary. | 38 KV (rms) |  |
|  | One minute power frequency withstand test voltage on secondary. | 2KV |  |
|  | Total creepage distance of the bushing. | >300 mm (min) |  |
|  | Live part to ground clearance. | >125 mm (min) |  |

- OUTDOOR CURRENT TRANSFORMER (CT) SPECIFIACATIONS

| Item No. | Particulars | RERE’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Transformation ratio | 50-25/1 |  |
|  | Standard reference | IEC |  |
|  | Rated Voltage (KV) | 11 |  |
|  | Frequency (Hz) | 50 |  |
|  | Rated Short time current for 1 min (kA) | 25 |  |
|  | Creepage Distance | ˃370 |  |
|  | Rated Continuous Thermal current (A) | 1, 2xIn |  |
|  | Number of Secondary windings | 2 |  |
|  | 1st winding |  |  |
|  | Rated primary current, In (A) | 50A and 25A |  |
|  | Rated Secondary current, (A) | 1 |  |
|  | Accuracy class | 0.5 |  |
|  | 2nd winding |  |  |
|  | Rated primary current, In (A) | 50A and 25A |  |
|  | Rated Secondary current, (A) | 1 |  |
|  | Accuracy class | 5P10 |  |

- OUTDOOR VOLTAGE TRANSFORMER (VT) SPECIFIACATIONS

| Item No. | Particulars | RERE’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Transformation ratio | 11000/110Vac |  |
|  | Standard reference | IEC |  |
|  | Rated Voltage (KV) | 11 |  |
|  | Frequency (Hz) | 50 |  |
|  | Thermal Burden, VA | 450 |  |
|  | Creepage Distance | ˃1000 |  |
|  | Number of Secondary windings | 2 |  |
|  | Rated output, VA | 50 |  |
|  | 1st winding |  |  |
|  | Rated primary voltage, KV | 11 |  |
|  | Rated Secondary Voltage, V | 110 |  |
|  | Accuracy class | 0.5 |  |
|  | 2nd winding |  |  |
|  | Rated primary voltage, KV | 11 |  |
|  | Rated Secondary Voltage, V | 110 |  |
|  | Accuracy class | 0.5 |  |

- 11KV SURGE DIVERTERS SPECIFICATIONS

| Item No. | Particulars | RERE’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Standard Reference | IEC |  |
|  | Normal system voltage, KV | 11 |  |
|  | Highest system voltage, KV | 12 |  |
|  | System fault level, kA | 20 |  |
|  | Line Discharge Class | 10 |  |
|  | Lighting Impulse Residual voltage, KV | 95 |  |

- ISOLATOR WITHOUT EARTH SWTCH

| Item No. | Particulars | RERE’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Standard Reference | IEC |  |
|  | Rated Voltage, KV | 12 |  |
|  | Rated Frequency, HZ | 50 |  |
|  | Rated lighting impulse withstand voltage, 1.2/50µS (KV) | 95 |  |
|  | Rated power frequency withstand voltage, Wet, 50HZ, 60secs (KV) | 38 |  |
|  | Minimum creepage distance of insulators, mm | 320 |  |
|  | Rated normal current, A | 800 |  |
|  | Rated short time withstand current for 3secs, Ka | 25 |  |

- ISOLATOR WITH EARTH SWITCH

| Item. | Particulars | RERE’S Requirement | Bidders Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Standard Reference | IEC |  |
|  | To be fitted with Earth Switch | To provide |  |
|  | Rated Voltage, KV | 11 |  |
|  | Rated Frequency, HZ | 50 |  |
|  | Rated lighting impulse withstand voltage, 1.2/50µS (KV) | 95 |  |
|  | Rated power frequency withstand voltage, Wet, 50HZ, 60secs (KV) | 38 |  |
|  | Minimum creepage distance of insulators, mm | 320 |  |
|  | Rated normal current, A | 800 |  |
|  | Rated short time withstand current for 3secs, kA | 25 |  |

- Rectifier- Battery Charger Technical Specification

| Item No. | Particulars | REREC’S Requirement | Bidder’s Response |
| --- | --- | --- | --- |
|  | Manufacturer | State |  |
|  | Model | State |  |
|  | Warranty | State |  |
|  | Input Data |  |  |
|  | Input Voltage | 240VAC+-10% |  |
|  | Inrush Current | <15In |  |
|  | Power factor | 0.8 |  |
|  | Frequency range | 47-63Hz |  |
|  | Output Data |  |  |
|  | Output Voltage range | 110-125VDC |  |
|  | Nominal Output voltage | 110VDC |  |
|  | Static Regulation | 1% |  |
|  | Voltage ripple 3-phase | (Disconnected battery) <0.7% |  |
|  | General data |  |  |
|  | Rectifier efficiency | 83%-94% |  |
|  | Operating temperature range | 0 to 40 degrees |  |
|  | Storage temperature | -20 to +70 degrees Celsius |  |
|  | Relative humidity | <95% non-condensing at 20 degrees Celcius |  |
|  | Operating altitude | 1000m without system duration |  |
|  | Cooling | Natural or fan assisted |  |
|  | Noise at 1m in front of the unit | 1dB |  |
|  | Protection | Protection against battery reversed polarity |  |
|  | Compliance | IEC 61000-6-4 |  |

SECTION VII

- ESIA CONSULTANCY

The key objective of this study is to conduct ESIA with a view to identify the critical environmental and social concerns in Kiwa and Kibwongi Islands solar PV minigrid, including the involved transmission line, and address them as an integral part of project design and obtain license from NEMA

The specific objective includes:

- To assess the existing environment and social status in the study area and area of influence  to identify threats and issues which have potential to adversely impact important environmental and social features of the project influence area.

- Carry out environmental and social analysis of solar PV Mini grid area and potential activities envisaged under the project, including internal evacuation infrastructure from the solar PV to sub-station.

- Conduct labour influx risk assessment and the key focus would be to assess impacts on local communities associated with the temporary influx of labour that typically results from construction works.

- Analyze various options available in the site layout and arrangements for ancillary facilities, like water supply, with special reference to sources – whether local groundwater or water from distant sources would be used; in case of the latter situation, conveyance facilities will also be analyzed for impacts, drainage, access, etc. to minimize adverse impacts and enhance positive impacts, where feasible.

- Identification of the project affected families; assessment of loss of livelihood / property resources for people living within the proposed site and in its immediate vicinity through primary surveys covering all project affected families/ consultations.

- Prepare a site-specific ESIA report by documenting environmental features of the project area, socio-economic and cultural status of community in and around the probable project site. This assessment should also include considerations of safety – both for the workers in the site and related facilities, as well as of nearby residents, especially those that live close to ancillary facilities like borrow areas.

- To identify the environmental and social issues associated with implementation of Solar PV Mini grid and develop environmental codes of practices for common activities, like site preparation, installation of panels, management of waste, occupational health and safety, etc. and social exclusion list that need to be followed during various stages, such as planning, construction and operation & maintenance.

ESIA Methodology

As a chapter of the ESIA report, the consultant will describe the methods used for conducting the ESIA (scoping and bounding, impact analysis and public consultation process, etc.). The consultant will include a public participation plan to include stakeholder identification process, stakeholders identified, stages within the ESIA process where stakeholders have participated, and the different levels of participation used. Identification of impacts will include the identification of the important environmental components, and selection criteria used for identifying the significant impacts (positive and negative) whenever possible. Significant levels may be determined through the application of a scoring system if the consultant feels that such an approach is warranted. The consultant will employ environmental economic analysis where applicable, particularly to justify significant impacts to be mitigated.

Potential Impacts of the Proposed Project

Using the collected baseline data and the system or monitoring and evaluation, the consultant will take a systematic approach to identification, mitigation and evaluation of all impacts and will identify potential changes which the proposed project may cause.

These would include, but not be limited to, changes in the following:

- Physical environment: geological, topography, soils climate and meteorological; ground water and surface hydrology

- Biological environment: flora, fauna; rare or endangered significant natural sites, etc; species of commercial importance and species with potential to become a nuisance, vector or dangerous.

- Socio-cultural environment. (Include both present and projected where appropriate); population affected (number of subsistence systems), land use where appropriate and property (including houses, crops/plants and other properties etc); planned development activities; public health; cultural characteristics (including cultural property and heritage); and gender differentiation.

- Economic activities: Livelihood; employment; gender composition. Some examples of the specific activities are based on field surveys; identification of any species of special concerns, namely species with conservation status of endemic to the area including birds; commentary on conservation status of specific species; complication of a broad scale vegetation or habitant map of the area indicating the extent to which the proposed project can affect each vegetation or habitant type; description of current land use and complication of a broad land use map.

- Employment opportunities.

- Safety issues, including (i) measures to assure safety of local residents in relation to project development activities (ii) ensure that the safety and health concerns of permanent, temporary and migrant workers are addressed and (iii) an HIV, AIDS program for workers and affected communities.

- Construction phase impacts.

- Waste management for the entire project, including the work camps and construction sites.

- Traffic density, safety and dust control.

- Land acquisition and resettlement as per national and international guidelines.

The Consultant will analyze:

- Positive and negative impacts.

- Direct and indirect impacts, short term and long term.

- Impacts that are avoidable/unavoidable; reversible/irreversible.

- Pre-construction actions to avoid or minimize negative impacts.

- Construction and operational phase impacts.

- Cumulative impacts occurring as a consequence of other activities in the project area: existing activities, projects under construction or planned activities within a reasonable time frame.

- Impacts in critical and non-critical habitats.

- Identify the potential risk of the spread of HIV/AIDS and other sexually transmitted diseases during the construction period, and prepare a detailed plan for awareness and prevention including resource implications.

- Wherever possible, the consultant will describe impacts quantitatively. In terms of environmental costs and benefits, and assign economic values when feasible. Impact analysis should be divided between construction and operation impacts.

Environmental and Social Management Plan

- An Environmental and Social Management Plan (ESMP) that addresses the following aspects should be prepared:

- Activities and impacts: Predicted adverse environmental and social impacts (and any uncertainties about their effects) for which mitigation is necessary should be identified and summarized. Effective measures to prevent or reduce significant negative impacts to acceptable levels during (i) construction and (ii) operation. Estimate the impacts and costs of those measures. Estimate the costs of any residual impacts. Another area of impacts that could contribute substantially are the cumulative effects of construction and operational phases of the Project. Most of these, if not all, can be avoided by following a set of best practices that the consultant will prepare.

- Description of implementation and monitoring program: Prepare a detailed arrangement (responsibilities) for implementing and for monitoring implementation of mitigation measures and the impacts of the project during construction and operation and maintenance. This will include a description of monitoring methodology, specific operations and features to be monitored, monitoring reporting relationships, and arrangements to ensure that monitoring is effective and leads to modifications where required to ensure minimal impact on the environment. Include in the plan an estimate of costs and description of other inputs such as training and institutional strengthening to ensure effective monitoring. An indication of what performance indicators to be used is to be provided.

- Institutional strengthening and training: Identification of institutional needs to implement environmental recommendations:

REPORTING

- The consultant will produce the following reports in draft and final versions:

- Environmental and Social Impact Assessment reports

- Environmental Management Plan

- Stakeholder Engagement Plan (SEP)/ Stakeholder Consultation Plan (SCP)

- Land Acquisition & Compensation Plan (LACP)/Resettlement Action Plan

- Executive Summary of Environmental and Social Impact Assessment Report – Final Report

# SECTION VIII: DRAWINGS AND TOOLS

- DRAWINGS

NO DRAWINGS WILL BE PROVIDED BY THE CLIENT

- Tools and Equipment’s

The Bidder must demonstrate that it will have access to the key equipment required to perform the contract.

| No. | Equipment Type and Characteristics | Minimum Number required |
| --- | --- | --- |
| 1 | Insulation resistance test set | One per lot |
| 2 | Earth resistance test set (electronic) | One per lot |
| 3 | Primary injection Kit | One per lot |
| 4 | Secondary Injection kit | One per lot |
| 5 | CMEs | One per lot |
| 6 | Digital Multimeter | One per lot |
| 7 | Digital clamp on meter | One per lot |
| 8 | Polarity tester/ earth leakage meter | One per lot |
| 9 | Battery Analyzer | One per lot |
| 10 | Tool box (Solar PV technician tool box). | One per Lot |
| 11 | Loop impedance tester | One per Lot |
| 12 | Insulation resistance tester | One per Lot |
| 13 | Cordless drill | One per Lot |
| 14 | Electric hand air blower | One per Lot |
| 15 | PPE and safety gear for the commissioning team | One per Lot |
| 16 | Variable Dummy Load Tester (For testing Full Load and Surge Capability of the system) | One per Lot |

NB:

- Bidder to fill form EQU for each of the tools and Equipment listed above.

- Successful bidder to avail the Tools necessary for system testing during commissioning exercise.

- Successful bidder to generate Test protocol and Test Sheet necessary for system testing and successful commissioning for employers approval.(Test should not be limited to Earth resistance test, Insulation Resistance test, Impedance Test, Earth Leakage current test, Load capacity test, Battery state of health test etc.).

# SECTION IX: BILLS OF QUANTITIES

The Bill of Quantities shall form part of the Contract Documents and is to be read in conjunction with the Instructions to Tenderers, Conditions of Contract Parts I and II, Specifications and Drawings.

The brief description of the items in the Bill of Quantities is purely for the purpose of identification, and in no way modifies or supersedes the detailed descriptions given in the conditions of Contract and Specifications for the full direction and description of work and materials.

The Quantities set forth in the Bill of Quantities are estimated and provisional, representing substantially the work to be carried out, and are given to provide a common basis for tendering and comparing of Tenders.  There is no guarantee to the Contractor that he will be required to carry out all the quantities of work indicated under any one particular item or group of items in the Bill of Quantities.  The basis of payment shall be the Contractor’s rates and the quantities of work actually done in fulfillment of his obligation under the Contract.

The prices and rates inserted in the Bills of Quantities will be used for valuing work executed, and the Engineer will measure the whole of the works executed in accordance with this Contract.

A price or rate shall be entered in ink against every item in the Bill of Quantities with the exception of items, which already have provisional sums, affixed thereto. The Tenderers are reminded that no “nil” or “included” rates or “lump-sum” discounts will be accepted.  The rates for various items should include discounts if any. Tenderers who fail to comply will be disqualified.

Provisional sums (including day works) in the Bill of Quantities shall be expended in whole or in part at the discretion of the Engineer in accordance with Sub-clause 52.4 and Clause 58 of part of the Conditions of Contract.

The price and rates entered in the Bill of Quantities shall, except insofar as it is otherwise provided under the Contract, include all Constructional plant to be used, labour, insurance, supervision, compliance, testing, materials, erection, maintenance or works, overheads and profits, taxes and duties together with all general risks, liabilities and obligations set out or implied in the Contract, transport, electricity and telephones, water, use and replenishment of all consumables, including those required under the Contract by the Engineer and his staff.

The Employer for any arithmetic errors in computation or summation will correct errors as follows:

Where there is a discrepancy between amount in words and figures, the amount in words will govern; and

Where there is a discrepancy between the unit rate and the total amount derived from the multiplication of the unit price and the quantity, the unit rate as quoted will govern, unless in the opinion of the Employer, there is an obviously gross misplacement of the decimal point in the unit price, in which event the total amount as quoted will govern and the unit rate will be corrected.

If a Tenderer does not accept the correction of errors as outlined above, his Tender will be rejected.

The Bills of Quantities, unless otherwise expressly stated therein, shall be deemed to have been prepared in accordance with the principles of the latest edition of the Civil Engineering Standard Method of Measurement (CESMM).

“Authorized” “Directed” or “Approved” shall mean the authority, direction or approval of the Engineer.

Unless otherwise stated, all measurements shall be net taken on the finished work carried out in accordance with the details shown on the drawings or instructed, with no allowance for extra cuts or fills, waste or additional thickness necessary to obtain the minimum finished thickness or dimensions required in this Contract.  Any work performed in excess or the requirements of the plans and specifications will not be paid for, unless ordered in writing by the Engineer.

Hard material, in this Contract, shall be defined as the material which, in the opinion of the Engineer, require blasting, or the use of metal wedges and sledgehammers, or the use of compressed air drilling for their removal, and which cannot be extracted by ripping with a dozer tractor of at least 150 brake horse power (112 kilowatt) with a single, rear-mounted, hydraulic ripper. Boulders of more than 0.2m3 occurring in soft material shall be classified as hard material. Soft material shall be all material other than hard material.

- PRICE SCHEDULE FOR LOT 1-KIWA ISLAND SOLAR MINIGRID

## CIVIL WORKS SPECIFICATIONS AND BILL OF QUANTITIES

Tender to provide layout plans and drawings for approval by employer before commencement of construction.

- FENCE

| CHAIN LINK FENCE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | QTY | RATE | AMOUNT |
| 1.2 | Compound fence |  |  |  |  |
| 1.2.1 | Provide all materials and install 2400mm high chain link fence above ground level consisting of 125x125x3000mm overall cranked precast concrete post (mix 1:2:4) to BS 1722 posts with 450mm long cranks at 3.0m centers reinforced with 4 No. 8mm diameter high tensile bars including 6mm diameter stirrups at 300 centers complete with 14 1/2 gauge x6 strand galvanized barbed wire fencing and mortised in mass concrete surround 1:3:6 including all excavations, formwork and disposals | LM | 640 |  | - |
| 1.2.2 | Extra over ditto; for 100x100mm precast concrete struts 2600mm long at every 50m interval | No. | 26 |  | - |
| 1.3 | Minigrid Palisade Gate |  |  |  | - |
|  | Supply and fix double leaf steel palisade gate with a passengers gate including building in lugs and jamb to concrete columns | LM | 4.8 |  |  |
| 1.4 | Solar PV Yard fence |  |  |  |  |
| 1.4.1 | Provide all materials and install 2400mm high chain link fence above ground level consisting of 125x125x3000mm overall cranked precast concrete post (mix 1:2:4) to BS 1722 posts with 450mm long cranks at 3.0m centers reinforced with 4 No. 8mm diameter high tensile bars including 6mm diameter stirrups at 300 centers complete with 14 1/2 gauge x6 strand galvanized barbed wire fencing and mortised in mass concrete surround 1:3:6 including all excavations, formwork and disposals. Allow for 1.5 M pedestrian Gate | LM | 300 |  |  |
| 1.4.5 | Extra over ditto; for 100x100mm precast concrete struts 2600mm long at every 50m interval | No. | 12 |  |  |
| 1.4.6 | Solar PV yard Gate |  |  |  |  |
|  | Supply and fix double leaf steel palisade gate with a passengers gate including building in lugs and jamb to concrete columns | LM | 3 |  |  |
| 4.5 | Substation fence |  |  |  |  |
| 1.5.1 | Provide all materials and install 2400mm high chain link fence above ground level consisting of 125x125x3000mm overall cranked precast concrete post (mix 1:2:4) to BS 1722 posts with 450mm long cranks at 3.0m centers reinforced with 4 No. 8mm diameter high tensile bars including 6mm diameter stirrups at 300 centers complete with 14 1/2 gauge x6 strand galvanized barbed wire fencing and mortised in mass concrete surround 1:3:6 including all excavations, formwork and disposals. Allow for 1.5 M pedestrian Gate | LM | 100 |  |  |
| 1.5.2 | Extra over ditto; for 100x100mm precast concrete struts 2600mm long at every corner | No. | 4 |  |  |
| 1.5.3 | Substation Gate |  |  |  |  |
|  | Supply and fix double leaf steel palisade gate with a passengers gate including building in lugs and jamb to concrete columns | LM | 3 |  |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  |

- Guard House

| CONTAINER OFFICE, EQUIPMENT ROOM, SUBSTATION WORKS,STORM WATER, DRAINAGE, WATER SUPPLY, FIRE PROTECTION & ACCESS ROAD |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | QTY | RATE |
| 4.1 | Planters or the Like |  |  |  |
| 4.1.1 | Excavate pits 1000X1000X500mm deep :part cart away, part back fill soil and manure mixture in 4.1 ratio | NO | 40 |  |
| 4.1.2 | Provide plant well established assorted plants including watering and weeding until well established | NO | 40 |  |
| 4.2 | Access road |  |  |  |
| 4.2.1 | Excavate in soil to remove top vegetable soil to 250mm deep | CM | 300 |  |
| 4.2.2 | Excavate to reduce levels in any type of soil 400mm deep | CM | 400 |  |
| 4.2.3 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 300 |  |
| 4.2.4 | Lay murram as finish compacted in layers not exceeding 150mm thick to 100% maximum dry density. With -2.5% camber in the access road to allow for drainage | CM | 200 |  |
| 4.2.5 | 125 x 250 mm Splayed kerb to BS 340 including 125 x 100 mm channel on and including concrete Class 'E' foundation and 200mm haunching to back of a kerb including all necessary excavation, formwork and disposal. | LM | 600 |  |
| 4.3 | Container Yard |  |  |  |
| 4.3.1 | Excavate in soil to remove top vegetable soil to 500mm deep | CM | 100 |  |
| 4.3.2 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 100 |  |
| 4.3.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers ( 100mm Thick) | CM | 60 |  |
| 4.4 | Water Supply |  |  |  |
| 4.4.1 | Supply and installation of one ground mounted 10,000 litres PVC water tank including construction of its base | No. | 1 |  |
| 4.4.2 | Supply and installation of one ground mounted 5,000 litres PVC water tank including construction of its base for storage of rain water harvested | No. | 1 |  |
| 4.4.3 | Allow for water reticulation from the nearest water source to the site storage tank. | LM | 400 |  |
| 4.4.4 | Allow for water reticulation from the storage tank to solar yard area and outside the office, Including installation of 2 taps. | LM | 30 |  |
| 4.5 | Office Container |  |  |  |
| 4.5.1 | Supply, deliver and install 20ft container on site and allow for modification of the container to an office with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations atleast 500mm above the original ground level including steps for accessing the container (to engineers Approval). | No. | 1 |  |
| 4.5.2 | Supply, deliver and install two 40ft container on site and allow for modification of the containers to an equipment room with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the containers (to engineers Approval). | No. | 2 |  |
| 4.5.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers (100mm thick) | CM | 14 |  |
| 4.5.4 | Supply and fix air conditioners in the equipment rooms and office container complete with all fixing accessories to control room temperatures from approved suppliers | No. | 5 |  |
| 4.6 | Furniture |  |  |  |
| 4.6.1 | One office Table | No. | 2 |  |
| 4.6.2 | Chairs | No. | 4 |  |
| 4.6.3 | Storage Cabinet ( Metal Drawers) Control house | No. | 1 |  |
| 4.7 | Allow for design and construction of stone pitched storm water drainage for the entire station including culverts to engineers approval | Sum | 1 |  |
| 4.8 | FIRE EXTINGUISHERS |  |  |  |
| 4.8.1 | Supply and fix controlled discharge 9Kg carbon dioxide gas fire extinguisher manufactured to BS EN 3-9:2006, Bs 7863:2009, BS 5306- 4:2001 and the cylinder manufactured to BS 5045 complete with the following: Charge and fixing bracket, pictorial instructions, colour code, serviceable on site, discharge horn and hose, Brass hot stamping, Operating valve, local Fire Bridge approval. | No | 1 |  |
| 4.8.2 | Ditto but DRY powder fire extinguishers | No | 4 |  |
| 5 | SUBSTATION WORKS |  |  |  |
| 5.1 | Supply of Transformer and any other equipment Plinth including laying of ballast at the substation at least 100mm as per approved Design of Plant | SUM | 1 |  |
| 5.2 | Cable trenches |  |  |  |
| 5.2.1 | provide cable trenches (600x500) length aprox. 100m at various Positions including HATARI slabs as per the approved layout | M | 100 |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |

- 2 DOOR VIP LATRINE

| ITEM | DESCRIPTION | UNITS | QTY | RATE |
| --- | --- | --- | --- | --- |
| 3.1 | Excavation and Earthworks |  |  |  |
| 3.1.1 | Clear site of all vegetation and small trees and dispose off Bulk excavations | SM | 10 |  |
| 3.1.2 | Excavation of a latrine pit not less than 5meters deep Planking and strutting | CM | 32 |  |
| 3.1.3 | Allow for Planking and strutting to sides of excavated pits: including removal of fallen materials Water disposal | ITEM | 1 |  |
| 3.1.4 | Allow for keeping all excavations from all types of water including rain and spring water by pumping or through any method | ITEM | 1 |  |
| 3.2 | Concrete Works |  |  |  |
| 3.2.1 | Supplying and placing of Grade 20 concrete as specified on 100mm thick beds | CM | 0.5 |  |
| 3.2.2 | Supplying and placing of Grade 25 concrete as specified in strip footings | CM | 1.1 |  |
| 3.2.3 | Ditto: suspended slabs: 150mm thick with a slab. Formwork | CM | 1.5 |  |
| 3.2.4 | Formwork as specified to vertical sides of strip footing | SM | 2 |  |
| 3.2.5 | Ditto: soffites of suspended slabs | SM | 5 |  |
| 3.2.6 | Ditto: edges of floor beds | SM | 3 |  |
| 3.2.7 | Boxing Formwork to form opening size 450 x 450mm for manhole | NO | 2 |  |
| 3.2.8 | Ditto: opening in slab size 200 x 300mm | NO | 2 |  |
| 3.2.9 | Ditto: opening in slab size 110mm diameter Reinforcement: (All provisional) | NO | 2 |  |
| 3.2.10 | Y12 high yield reinforcement bars with 6mm diameter links at 200mm c/c. | KG | 145 |  |
| 3.2.11 | Lintel size 200 x 150 mm in cross section: including 4No. Y10 bars and R 6 links at 200mm centers complete with all formwork: as per Drawing. | LM | 10 |  |
| 3.3 | Masonry Works |  |  |  |
| 3.3.1 | Up to DPC level-Substructure (Lining) 200 mm Thick solid block walls: bedded and jointed in cement and sand (1:4 ) mortar to lining. Reinforced with iron wall ties at every alternate course | SM | 52 |  |
|  | Concrete block work |  |  |  |
| 3.3.2 | 200mm thick walls in blocks in cement sand (1:3) mortar: reinforced with hoop iron wall ties at every alternate course Damp proof course | SM | 31 |  |
| 3.3.3 | Horizontal damp proof course: bituminous: laid horizontally on screed 20 mm thick (1:3) screed beds to receive block walls. | LM | 10 |  |
|  | Roof structures |  |  |  |
| 3.3.4 | Supply & fix seasoned timber (cypress) for roof trusses( 100 x50mm) and purlins (75 x50mm) complete with all the required paint works and all necessary supports | ITEM | 1 |  |
| 3.4 | Roof Covering |  |  |  |
| 3.4.1 | Supplying & fixing of gauge 28 pre-painted IT5 box profiled roofing sheets (0.32mm) of approved colour Nailed to 75x50 timber purlins (measured separately) | SM | 6 |  |
|  | Valance / Barge Board |  |  |  |
| 3.4.2 | 25x225mm high timber valance board / barge board Nailed to 75x50 timber purlins: all complete with approved wood preservative as specified and as per | LM | 10 |  |
| 3.5.1 | Doors |  |  |  |
|  | Steel Door: to fit structural opening size 900mm wide x 2100mm high overall, comprising of 50 x 50x4mm Angle iron door frame: including all iron mongery and hardware: fixed to concrete or block work: complete with all required painting and decoration | NO | 2 |  |
| 3.5.2 | Manhole cover |  |  |  |
|  | Supply and install 450 x 450 mm mild steel man hole cover | NO | 1 |  |
| 3.6 | Ventilation |  |  |  |
|  | Vent pipes |  |  |  |
|  | Supply and install 2 (two) vent pipes- 110mm diameter and at least 300mm above the highest point of the roof | NO | 2 |  |
| 3.7 | Finishes |  |  |  |
|  | Wall Finishes |  |  |  |
| 3.7.1 | 15mm thick wood float finished render 1:4 below window sill | SM | 1 |  |
| 3.7.2 | Ditto to lintel and walls | SM | 0.5 |  |
| 3.7.3 | Recessed horizontal key pointing to brick walls | SM | 21 |  |
| 3.7.4 | 15mm thick two coat lime plaster to walls Floor finishes | SM | 21 |  |
| 3.7.5 | 40 mm thick colored cement sand (1:4) screed finished smooth including hardener additive | SM | 6 |  |
| 3.7.6 | Ditto but 150x10mm skirting | SM | 5 |  |
| 3.8 | Painting |  |  |  |
| 3.8.1 | Painting and decoration Preparing and apply three coats plastic silk emulsion paint to: Plastered walls internally | SM | 33 |  |
| 3.8.2 | Prepare and apply three coat matt enamel paint to: General surfaces of metal doors | SM | 8 |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |

- CONTAINER OFFICE, DRAINAGE, WATER SUPPLY & ACCESS ROAD

| CONTAINER OFFICE, EQUIPMENT ROOM, SUBSTATION WORKS,STORM WATER, DRAINAGE, WATER SUPPLY, FIRE PROTECTION & ACCESS ROAD |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | QTY | RATE |
| 4.1 | Planters or the Like |  |  |  |
| 4.1.1 | Excavate pits 1000X1000X500mm deep:part cart away, part back fill soil and manure mixture in 4.1 ratio | NO | 40 |  |
| 4.1.2 | Provide plant well established assorted plants including watering and weeding until well established | NO | 40 |  |
| 4.2 | Access road |  |  |  |
| 4.2.1 | Excavate in soil to remove top vegetable soil to 250mm deep | CM | 300 |  |
| 4.2.2 | Excavate to reduce levels in any type of soil 400mm deep | CM | 400 |  |
| 4.2.3 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 300 |  |
| 4.2.4 | Lay murram as finish compacted in layers not exceeding 150mm thick to 100% maximum dry density. With -2.5% camber in the access road to allow for drainage | CM | 200 |  |
| 4.2.5 | 125 x 250 mm Splayed kerb to BS 340 including 125 x 100 mm channel on and including concrete Class 'E' foundation and 200mm haunching to back of a kerb including all necessary excavation, formwork and disposal. | LM | 600 |  |
| 4.3 | Container Yard |  |  |  |
| 4.3.1 | Excavate in soil to remove top vegetable soil to 500mm deep | CM | 100 |  |
| 4.3.2 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 100 |  |
| 4.3.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers ( 100mm Thick) | CM | 60 |  |
| 4.4 | Water Supply |  |  |  |
| 4.4.1 | Supply and installation of one ground mounted 10,000 litres PVC water tank including construction of its base | No. | 1 |  |
| 4.4.2 | Supply and installation of one ground mounted 5,000 litres PVC water tank including construction of its base for storage of rain water harvested | No. | 1 |  |
| 4.4.3 | Allow for water reticulation from the nearest water source to the site storage tank. | LM | 400 |  |
| 4.4.4 | Allow for water reticulation from the storage tank to solar yard area and outside the office, Including installation of 2 taps. | LM | 30 |  |
| 4.5 | Office Container |  |  |  |
| 4.5.1 | Supply, deliver and install 20ft container on site and allow for modification of the container to an office with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the container (to engineers Approval). | No. | 1 |  |
| 4.5.2 | Supply, deliver and install two 40ft container on site and allow for modification of the containers to an equipment room with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the containers (to engineers Approval). | No. | 2 |  |
| 4.5.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers (100mm thick) | CM | 14 |  |
| 4.5.4 | Supply and fix air conditioners in the equipment rooms and office container complete with all fixing accessories to control room temperatures from approved suppliers | No. | 5 |  |
| 4.6 | Furniture |  |  |  |
| 4.6.1 | Office Table | No. | 2 |  |
| 4.6.2 | Chairs | No. | 4 |  |
| 4.6.3 | Storage Cabinet ( Metal Drawers) Control house | No. | 1 |  |
| 4.7 | Allow for design and construction of stone pitched storm water drainage for the entire station including culverts to engineers approval | Sum | 1 |  |
| 4.8 | FIRE EXTINGUISHERS |  |  |  |
| 4.8.1 | Supply and fix controlled discharge 9Kg carbon dioxide gas fire extinguisher manufactured to BS EN 3-9:2006, Bs 7863:2009, BS 5306- 4:2001 and the cylinder manufactured to BS 5045 complete with the following: Charge and fixing bracket, pictorial instructions, color code, serviceable on site, discharge horn and hose, Brass hot stamping, Operating valve, local Fire Bridge approval. | No | 1 |  |
| 4.8.2 | Ditto but DRY powder fire extinguishers | No | 4 |  |
| 5 | SUBSTATION WORKS |  |  |  |
| 5.1 | Supply of Transformer and any other equipment Plinth including laying of ballast at the substation at least 100mm as per approved Design of Plant | SUM | 1 |  |
| 5.2 | Cable trenches |  |  |  |
| 5.2.1 | provide cable trenches (600x500) length approximately 100m at various Positions including HATARI slabs as per the approved layout | M | 100 |  |
| 6 | GENERATOR HOUSING |  |  |  |
| 6.1 | 5500mm long*4500mm wide Generator housing comprising of a stub masonry wall, mild steel grill comprising of 50*25*3mm RHS framings, vertical standards at 600mm centers, balusters size 20*20*3mm RHS at 150mm centers including welding and priming with red oxide, a double leaf mild steel door size 1500*3000mm and gauge 28 IT5 box profile roof. | SUM | 1 |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |

| GRAND SUMMARY FOR CIVIL |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | AMOUNT (KSH) |
| 1 | Chain Link Fence |  |
| 2 | Guard House |  |
| 3 | 2 door pit latrine |  |
| 4 | Container Office, Equipment Room, Substation Works, Storm Water, Drainage, Water Supply, Fire Protection & Access Road |  |
| SUB TOTAL |  |  |
| ADD 16% VAT |  |  |
| SUBTOTAL |  |  |
| GRAND TOTAL for Civil works (Item 1) |  |  |

- BILL OF QUANTITIES AND PRICE SCHEDULE FOR STEP UP SUBSTATION

| Item | Description | Unit | Qty | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- |
|  | CURRENCY: |  |  |  |  |
| 1 | Control Panels (Set with 1 Incomer and 1 Feeder) as per the requirement. | Set | 1 |  |  |
| 2 | Energy Meter (Tariff type, 415V three phase meter) For Feeder | No. | 1 |  |  |
| 3 | Cabling and Earthing for the step-up transformer and the outdoor equipment. The Transformer will be approximately 35 meters from the control room. (Cable size 240mm sq) and associated cable tray or trenches. Control Panels will be placed inside the inverter room. The bidder will provide all control and power cables for all equipment’s | No. | 1 |  |  |
| 4 | Step-up transformer 315 KVA, 0.415/11 KV Step-up TX, fitted with Buchholz relay, and pressure relief valve (See specs) | No. | 1 |  |  |
| 5 | 11 KV Circuit Breaker (Triple Pole) complete with indoor Control and Protective relay panel and its accessories | No. | 1 |  |  |
| 6 | Outdoor Neutral current transformer (NCT) as per the requirement | No. | 1 |  |  |
| 7 | 11Kv Outdoor Current Transformers (CT) as per the requirement | No. | 3 |  |  |
| 8 | 11Kv Outdoor Voltage Transformers (VT) as per the requirement | No. | 3 |  |  |
| 9 | 11kv Lighting Arrester (LA)/ Surge Diverters | No. | 3 |  |  |
| 10 | 11Kv Isolator without Earth Switch (DS) | Set | 1 |  |  |
| 11 | 11Kv Isolator with Earth Switch (DSE) | Set | 1 |  |  |
| 12 | Mounting Structures for CT, VT, LA, DS and DSE | Set | 1 |  |  |
| 13 | 110VDC battery Bank supply | Set | 1 |  |  |
| 14 | 110VDC, 100AH Battery Charger | Set | 1 |  |  |
| 15 | Laptop computer fully loaded with the relays software initially stated in the specs. | Lot | 1 |  |  |
|  | SUB-TOTAL |  |  |  |  |
|  | ADD 16% VAT |  |  |  |  |
|  | TOTAL COST |  |  |  |  |

- 120 KWp SOLAR PV SYSTEM

| Item | Description | Unit | Qty | Unit Price | Total |
| --- | --- | --- | --- | --- | --- |
|  | Supply of Solar PV modules with junction box , Bypass Diodes, cable and MC4 connecter for inter connection with other module along with galvanized steel nuts & bolts for fixing up with module mounting structure as per the requirement & technical specification | KWp | 120 |  |  |
|  | Supply of hot dip galvanized MS steel/Aluminum Anodized made module-mounting structures(MMS) for above Modules of 120KWp capacity for holding modules including all necessary nuts and bolts as well as necessary clamps, foundations bolts etc as per requirements and technical specifications and duly approved design by REREC | Lot | 1 |  |  |
|  | Supply of 600/1000v DC Distribution Board for Power distribution /Accumulation at DC side with MCBS/MCCBS protection system/Surge protection System | Lot | 1 |  |  |
|  | Supply, and installation of 40kW Hybrid Inverters, for conversion of Solar generation along with all protections and controlling arrangement for integration with BESS and DG along with AC Distribution Board for accumulation on AC side and equipment for remote monitoring facilities as per the requirement & technical specification. | No | 3 |  |  |
|  | Supply and install a 3-phase 50KVA power output diesel generator with 415 V at 50 Hz. It should include a highly corrosion resistant enclosure, control panel and monitoring, fuel tank and circuit breaker protection. The diesel generator shall be suitable for indoor or outdoor installation and shall perform accordingly with the battery inverter and the system design. The diesel generator shall work in a fully automatic manner with the above stated component | Set | 1 |  |  |
|  | Supply of at least 361KWh minimum Lithium-ion Battery Conforming to IEC62619 standard applicable to battery technology, Long life (10 years minimum) Complete in all respect and conforming to Requirement & technical specifications. All these enclosed in standard 40 feet steel container with ready to use air- conditioned battery room. | KWh | 361 |  |  |
|  | Cabling complete with all necessary accessories for connection of solar modules to battery bank, inverter, to intelligent controller/manager and to agreed connection point at the station through an energy meter and generator to the battery bank. This to also include cabling from the diesel generator for integration with power from the solar plant. | Lot | 1 |  |  |
|  | Supply of galvanized steel trays for cabling installation including all necessary nuts and bolts for Installation as per requirement of approved design as per Employer’s requirements and Technical specification | Lot | 1 |  |  |
|  | Supply of Early Streamer Emissions (E S E) Terminals with fulfilment of Standards UNE21186 and NF c 17102 to protect the arrays yard area and buildings against lightning protection as per approved design along with clamps and masts of requisite height. | Lot | 1 |  |  |
|  | Supply and install SCADA along all associated equipment, Data acquisition, data logger, Display Unit and industrial type PC with remote data monitoring. | Lot | 1 |  |  |
|  | Supply and install Weather monitoring system to check solar irradiation, wind speed and ambient temperature and integrate it with SCADA system. | Lot | 1 |  |  |
|  | Supply and install Security equipment including IP night vision 4 no’s Long vision Telescopic Closed Circuit Television (CCTV),IR motion sensors and 2 no’s short vision camera CCTV cameras with Video display at the control room | Lot | 1 |  |  |
|  | Laptop computer fully loaded with software for remote monitoring(to be use by REREC to monitor solar plant) | No | 1 |  |  |
|  | Sub-Total(Non Vatable Materials) |  |  |  |  |
|  | Sub-Total(Vatable Materials) |  |  |  |  |
|  | ADD 16% VAT (Only goods that attract VAT) |  |  |  |  |
|  | Total Cost For Solar Plant |  |  |  |  |

- Tools and Critical spares

| Item | Description | Unit | Qty | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- |
|  | Tools |  |  |  |  |
| 1 | Electrical Workshop 55+ Piece Inlay Tool Set with case | No | 1 |  |  |
| 2 | Mechanical Workshop 450+ Pieces (Cr-V) Drawer Tool Trolley (with plastic/foam modular inlay tool control system) –robust, sturdy and lockable. | No | 1 |  |  |
| 3 | Electric Hand Drill Chuck Capacity Of 1.5 – 13 Mm With Case | No | 1 |  |  |
| 4 | Angle Grinder 4 ½ ’’ with case | No | 1 |  |  |
| 5 | Electric Blower 800w | No | 1 |  |  |
| 6 | Electrical Digital Multi Meter | No | 2 |  |  |
| 7 | Electrical Clamp-On Meter | NO | 2 |  |  |
|  | Critical Spares |  |  |  |  |
| 1 | Fan belt | No | 2 |  |  |
| 2 | Air filter | No | 4 |  |  |
| 3 | Thermostat | No | 1 |  |  |
| 4 | Oil filter | No | 10 |  |  |
| 5 | Fuel filter | No | 10 |  |  |
| 6 | Engine Oil (litres) | No | 210 |  |  |
| 7 | Engine additive (litres) | No | 10 |  |  |
| 8 | Diodes set | No | I set |  |  |
| 9 | AVR | No | 1 |  |  |
| 10 | Electronic Fuel Control Units (Governor) | No | 1 |  |  |
|  | SUB-TOTAL |  |  |  |  |
|  | ADD 16% VAT (Only goods that attract VAT) |  |  |  |  |
| Total For Tools And Critical Spares |  |  |  |  |  |

- Services

| Item | Description | Unit | Qty | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- |
|  | Transport all to the station, installation, testing and commissioning of all equipment under supervision of REREC | Lot | 1 |  |  |
|  | Operation for 1 month inclusive of 1 month operator training. |  |  |  |  |
|  | 12 Months maintenance plus training of maintenance staff. | Lot | 1 |  |  |
|  | Factory acceptance test for the distribution board and outdoor Switchgear for 2 REREC/KPLC engineers. | Lot | 1 |  |  |
|  | Factory acceptance test for the transformer for 2 REREC/KPLC engineers. | Lot | 1 |  |  |
|  | Factory acceptance test for the Solar Modules for 2 REREC/KPLC engineers | Lot | 1 |  |  |
|  | Factory acceptance test for the Inverters for 2 REREC/KPLC engineers | Lot | 1 |  |  |
|  | Factory acceptance test for the lithium ion batteries for 2 REREC/KPLC engineers | Lot | 1 |  |  |
|  | Sub Total |  |  |  |  |
|  | Add 16% VAT |  |  |  |  |
|  | Total for Services |  |  |  |  |

COST SUMMARY TO BE TRANSFERRED TO FORM OF TENDER AND ITEM TAB IN SRM SYSTEM

| KIWA ISLAND SOLAR POWER MINI GRID |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT |
| 1 | Total Civil Works, | Sum | 1 |  |  |
| 2 | Total Substation works | Sum | 1 |  |  |
| 3 | Total 120kW Solar Power Generation plant equipment | Sum | 1 |  |  |
| 4 | Tools and Critical spares | Sum | 1 |  |  |
| 5 | Total Services | Sum | 1 |  |  |
| 6 | 5% Contingency(to be used with the approval of the Project Manager) | Sum | 1 |  |  |
|  | GRAND TOTAL |  |  |  |  |

- PRICE SCHEDULE FOR LOT 2-KIBWONGI ISLAND SOLAR MINIGRID

- CIVIL WORKS SPECIFICATIONS AND BILL OF QUANTITIES

Tender to provide layout plans and drawings for approval by employer before commencement of construction.

- FENCE

| CHAIN LINK FENCE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | QTY | RATE | AMOUNT |
| 1.2 | Compound fence |  |  |  |  |
| 1.2.1 | Provide all materials and install 2400mm high chain link fence above ground level consisting of 125x125x3000mm overall cranked precast concrete post (mix 1:2:4) to BS 1722 posts with 450mm long cranks at 3.0m centers reinforced with 4 No. 8mm diameter high tensile bars including 6mm diameter stirrups at 300 centers complete with 14 1/2 gauge x6 strand galvanized barbed wire fencing and mortised in mass concrete surround 1:3:6 including all excavations, formwork and disposals | LM | 640 |  | - |
| 1.2.2 | Extra over ditto; for 100x100mm precast concrete struts 2600mm long at every 50m interval | No. | 26 |  | - |
| 1.3 | Minigrid Palisade Gate |  |  |  | - |
|  | Supply and fix double leaf steel palisade gate with a passengers gate including building in lugs and jamb to concrete columns | LM | 4.8 |  |  |
| 1.4 | Solar PV Yard fence |  |  |  |  |
| 1.4.1 | Provide all materials and install 2400mm high chain link fence above ground level consisting of 125x125x3000mm overall cranked precast concrete post (mix 1:2:4) to BS 1722 posts with 450mm long cranks at 3.0m centers reinforced with 4 No. 8mm diameter high tensile bars including 6mm diameter stirrups at 300 centers complete with 14 1/2 gauge x6 strand galvanized barbed wire fencing and mortised in mass concrete surround 1:3:6 including all excavations, formwork and disposals. Allow for 1.5 M pedestrian Gate | LM | 300 |  |  |
| 1.4.5 | Extra over ditto; for 100x100mm precast concrete struts 2600mm long at every 50m interval | No. | 12 |  |  |
| 1.4.6 | Solar PV yard Gate |  |  |  |  |
|  | Supply and fix double leaf steel palisade gate with a passenger’s gate including building in lugs and jamb to concrete columns | LM | 3 |  |  |
| 4.5 | Substation fence |  |  |  |  |
| 1.5.1 | Provide all materials and install 2400mm high chain link fence above ground level consisting of 125x125x3000mm overall cranked precast concrete post (mix 1:2:4) to BS 1722 posts with 450mm long cranks at 3.0m centers reinforced with 4 No. 8mm diameter high tensile bars including 6mm diameter stirrups at 300 centers complete with 14 1/2 gauge x6 strand galvanized barbed wire fencing and mortised in mass concrete surround 1:3:6 including all excavations, formwork and disposals. Allow for 1.5 M pedestrian Gate | LM | 100 |  |  |
| 1.5.2 | Extra over ditto; for 100x100mm precast concrete struts 2600mm long at every corner | No. | 4 |  |  |
| 1.5.3 | Substation Gate |  |  |  |  |
|  | Supply and fix double leaf steel palisade gate with a passengers gate including building in lugs and jamb to concrete columns | LM | 3 |  |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  |

- Guard House

| CONTAINER OFFICE, EQUIPMENT ROOM, SUBSTATION WORKS,STORM WATER, DRAINAGE, WATER SUPPLY, FIRE PROTECTION & ACCESS ROAD |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | QTY | RATE |
| 4.1 | Planters or the Like |  |  |  |
| 4.1.1 | Excavate pits 1000X1000X500mm deep :part cart away, part back fill soil and manure mixture in 4.1 ratio | NO | 40 |  |
| 4.1.2 | Provide plant well established assorted plants including watering and weeding until well established | NO | 40 |  |
| 4.2 | Access road |  |  |  |
| 4.2.1 | Excavate in soil to remove top vegetable soil to 250mm deep | CM | 300 |  |
| 4.2.2 | Excavate to reduce levels in any type of soil 400mm deep | CM | 400 |  |
| 4.2.3 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 300 |  |
| 4.2.4 | Lay murram as finish compacted in layers not exceeding 150mm thick to 100% maximum dry density. With -2.5% camber in the access road to allow for drainage | CM | 200 |  |
| 4.2.5 | 125 x 250 mm Splayed kerb to BS 340 including 125 x 100 mm channel on and including concrete Class 'E' foundation and 200mm haunching to back of a kerb including all necessary excavation, formwork and disposal. | LM | 600 |  |
| 4.3 | Container Yard |  |  |  |
| 4.3.1 | Excavate in soil to remove top vegetable soil to 500mm deep | CM | 100 |  |
| 4.3.2 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 100 |  |
| 4.3.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers ( 100mm Thick) | CM | 60 |  |
| 4.4 | Water Supply |  |  |  |
| 4.4.1 | Supply and installation of one ground mounted 10,000 litres PVC water tank including construction of its base | No. | 1 |  |
| 4.4.2 | Supply and installation of one ground mounted 5,000 litres PVC water tank including construction of its base for storage of rain water harvested | No. | 1 |  |
| 4.4.3 | Allow for water reticulation from the nearest water source to the site storage tank. | LM | 400 |  |
| 4.4.4 | Allow for water reticulation from the storage tank to solar yard area and outside the office, Including installation of 2 taps. | LM | 30 |  |
| 4.5 | Office Container |  |  |  |
| 4.5.1 | Supply, deliver and install 20ft container on site and allow for modification of the container to an office with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the container (to engineers Approval). | No. | 1 |  |
| 4.5.2 | Supply, deliver and install two 40ft container on site and allow for modification of the containers to an equipment room with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the containers (to engineers Approval). | No. | 2 |  |
| 4.5.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers (100mm thick) | CM | 14 |  |
| 4.5.4 | Supply and fix air conditioners in the equipment rooms and office container complete with all fixing accessories to control room temperatures from approved suppliers | No. | 5 |  |
| 4.6 | Furniture |  |  |  |
| 4.6.1 | One office Table | No. | 2 |  |
| 4.6.2 | Chairs | No. | 4 |  |
| 4.6.3 | Storage Cabinet ( Metal Drawers) Control house | No. | 1 |  |
| 4.7 | Allow for design and construction of stone pitched storm water drainage for the entire station including culverts to engineers approval | Sum | 1 |  |
| 4.8 | FIRE EXTINGUISHERS |  |  |  |
| 4.8.1 | Supply and fix controlled discharge 9Kg carbon dioxide gas fire extinguisher manufactured to BS EN 3-9:2006, Bs 7863:2009, BS 5306- 4:2001 and the cylinder manufactured to BS 5045 complete with the following: Charge and fixing bracket, pictorial instructions, colour code, serviceable on site, discharge horn and hose, Brass hot stamping, Operating valve, local Fire Bridge approval. | No | 1 |  |
| 4.8.2 | Ditto but DRY powder fire extinguishers | No | 4 |  |
| 5 | SUBSTATION WORKS |  |  |  |
| 5.1 | Supply of Transformer and any other equipment Plinth including laying of ballast at the substation at least 100mm as per approved Design of Plant | SUM | 1 |  |
| 5.2 | Cable trenches |  |  |  |
| 5.2.1 | provide cable trenches (600x500) length approx. 100m at various Positions including HATARI slabs as per the approved layout | M | 100 |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |

- 2 DOOR VIP LATRINE

| ITEM | DESCRIPTION | UNITS | QTY | RATE |
| --- | --- | --- | --- | --- |
| 3.1 | Excavation and Earthworks |  |  |  |
| 3.1.1 | Clear site of all vegetation and small trees and dispose off Bulk excavations | SM | 10 |  |
| 3.1.2 | Excavation of a latrine pit not less than 5meters deep Planking and strutting | CM | 32 |  |
| 3.1.3 | Allow for Planking and strutting to sides of excavated pits: including removal of fallen materials Water disposal | ITEM | 1 |  |
| 3.1.4 | Allow for keeping all excavations from all types of water including rain and spring water by pumping or through any method | ITEM | 1 |  |
| 3.2 | Concrete Works |  |  |  |
| 3.2.1 | Supplying and placing of Grade 20 concrete as specified on 100mm thick beds | CM | 0.5 |  |
| 3.2.2 | Supplying and placing of Grade 25 concrete as specified in strip footings | CM | 1.1 |  |
| 3.2.3 | Ditto: suspended slabs: 150mm thick with a slab. Formwork | CM | 1.5 |  |
| 3.2.4 | Formwork as specified to vertical sides of strip footing | SM | 2 |  |
| 3.2.5 | Ditto: soffites of suspended slabs | SM | 5 |  |
| 3.2.6 | Ditto: edges of floor beds | SM | 3 |  |
| 3.2.7 | Boxing Formwork to form opening size 450 x 450mm for manhole | NO | 2 |  |
| 3.2.8 | Ditto: opening in slab size 200 x 300mm | NO | 2 |  |
| 3.2.9 | Ditto: opening in slab size 110mm diameter Reinforcement: (All provisional) | NO | 2 |  |
| 3.2.10 | Y12 high yield reinforcement bars with 6mm diameter links at 200mm c/c. | KG | 145 |  |
| 3.2.11 | Lintel size 200 x 150 mm in cross section: including 4No. Y10 bars and R 6 links at 200mm centers complete with all formwork: as per Drawing. | LM | 10 |  |
| 3.3 | Masonry Works |  |  |  |
| 3.3.1 | Up to DPC level-Substructure (Lining) 200 mm Thick solid block walls: bedded and jointed in cement and sand (1:4 ) mortar to lining. Reinforced with oop iron wall ties at every alternate course | SM | 52 |  |
|  | Concrete block work |  |  |  |
| 3.3.2 | 200mm thick walls in blocks in cement sand (1:3) mortar: reinforced with hoop iron wall ties at every alternate course Damp proof course | SM | 31 |  |
| 3.3.3 | Horizontal damp proof course: bituminous: laid horizontally on screed 20 mm thick (1:3) screed beds to receive block walls. | LM | 10 |  |
|  | Roof structures |  |  |  |
| 3.3.4 | Supply & fix seasoned timber (cypress) for roof trusses( 100 x50mm) and purlins (75 x50mm) complete with all the required paint works and all necessary supports | ITEM | 1 |  |
| 3.4 | Roof Covering |  |  |  |
| 3.4.1 | Supplying & fixing of gauge 28 pre-painted IT5 box profiled roofing sheets ( 0.32mm ) of approved colour Nailed to 75x50 timber purlins ( measured separately) : | SM | 6 |  |
|  | Valance / Barge Board |  |  |  |
| 3.4.2 | 25x225mm high timber valance board / barge board Nailed to 75x50 timber purlins: all complete with approved wood preservative as specified and as per | LM | 10 |  |
| 3.5.1 | Doors |  |  |  |
|  | Steel Door: to fit structural opening size 900mm wide x 2100mm high overall, comprising of 50 x 50x4mm Angle iron door frame: including all iron mongery and hardware: fixed to concrete or block work: complete with all required painting and decoration | NO | 2 |  |
| 3.5.2 | Manhole cover |  |  |  |
|  | Supply and install 450 x 450 mm mild steel man hole cover | NO | 1 |  |
| 3.6 | Ventilation |  |  |  |
|  | Vent pipes |  |  |  |
|  | Supply and install 2 (two) vent pipes- 110mm diameter and at least 300mm above the highest point of the roof | NO | 2 |  |
| 3.7 | Finishes |  |  |  |
|  | Wall Finishes |  |  |  |
| 3.7.1 | 15mm thick wood float finished render 1:4 below window sill | SM | 1 |  |
| 3.7.2 | Ditto to lintel and walls | SM | 0.5 |  |
| 3.7.3 | Recessed horizontal key pointing to brick walls | SM | 21 |  |
| 3.7.4 | 15mm thick two coat lime plaster to walls Floor finishes | SM | 21 |  |
| 3.7.5 | 40 mm thick coloured cement sand (1:4) screed finished smooth including hardener additive | SM | 6 |  |
| 3.7.6 | Ditto but 150x10mm skirting | SM | 5 |  |
| 3.8 | Painting |  |  |  |
| 3.8.1 | Painting and decoration Preparing and apply three coats plastic silk emulsion paint to: Plastered walls internally | SM | 33 |  |
| 3.8.2 | Prepare and apply three coat matt enamel paint to: General surfaces of metal doors | SM | 8 |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |

- CONTAINER OFFICE, DRAINAGE, WATER SUPPLY & ACCESS ROAD

| CONTAINER OFFICE, EQUIPMENT ROOM, SUBSTATION WORKS,STORM WATER, DRAINAGE, WATER SUPPLY, FIRE PROTECTION & ACCESS ROAD |  |  |  |  |
| --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNITS | QTY | RATE |
| 4.1 | Planters or the Like |  |  |  |
| 4.1.1 | Excavate pits 1000X1000X500mm deep :part cart away, part back fill soil and manure mixture in 4.1 ratio | NO | 40 |  |
| 4.1.2 | Provide plant well established assorted plants including watering and weeding until well established | NO | 40 |  |
| 4.2 | Access road |  |  |  |
| 4.2.1 | Excavate in soil to remove top vegetable soil to 250mm deep | CM | 300 |  |
| 4.2.2 | Excavate to reduce levels in any type of soil 400mm deep | CM | 400 |  |
| 4.2.3 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 300 |  |
| 4.2.4 | Lay murram as finish compacted in layers not exceeding 150mm thick to 100% maximum dry density. With -2.5% camber in the access road to allow for drainage | CM | 200 |  |
| 4.2.5 | 125 x 250 mm Splayed kerb to BS 340 including 125 x 100 mm channel on and including concrete Class 'E' foundation and 200mm haunching to back of a kerb including all necessary excavation, formwork and disposal. | LM | 600 |  |
| 4.3 | Container Yard |  |  |  |
| 4.3.1 | Excavate in soil to remove top vegetable soil to 500mm deep | CM | 100 |  |
| 4.3.2 | Back fill excavated areas with approved hardcore compacted in layers not exceeding 150mm thick to 100% maximum dry density. As base for the access road and parking | CM | 100 |  |
| 4.3.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers (100mm Thick) | CM | 60 |  |
| 4.4 | Water Supply |  |  |  |
| 4.4.1 | Supply and installation of one ground mounted 10,000 litres PVC water tank including construction of its base | No. | 1 |  |
| 4.4.2 | Supply and installation of one ground mounted 5,000 litres PVC water tank including construction of its base for storage of rain water harvested | No. | 1 |  |
| 4.4.3 | Allow for water reticulation from the nearest water source to the site storage tank. | LM | 400 |  |
| 4.4.4 | Allow for water reticulation from the storage tank to solar yard area and outside the office, Including installation of 2 taps. | LM | 30 |  |
| 4.5 | Office Container |  |  |  |
| 4.5.1 | Supply, deliver and install 20ft container on site and allow for modification of the container to an office with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the container (to engineers Approval). | No. | 1 |  |
| 4.5.2 | Supply, deliver and install two 40ft container on site and allow for modification of the containers to an equipment room with box profile gauge 28 IT5 roof and installation of gutters and down pipe for rain water harvesting, casting 400mm wide strip foundations at least 500mm above the original ground level including steps for accessing the containers (to engineers Approval). | No. | 2 |  |
| 4.5.3 | Supply, Deliver and spread 3/4 Ballast under and around the containers (100mm thick) | CM | 14 |  |
| 4.5.4 | Supply and fix air conditioners in the equipment rooms and office container complete with all fixing accessories to control room temperatures from approved suppliers | No. | 5 |  |
| 4.6 | Furniture |  |  |  |
| 4.6.1 | Office Table | No. | 2 |  |
| 4.6.2 | Chairs | No. | 4 |  |
| 4.6.3 | Storage Cabinet ( Metal Drawers) Control house | No. | 1 |  |
| 4.7 | Allow for design and construction of stone pitched storm water drainage for the entire station including culverts to engineers approval | Sum | 1 |  |
| 4.8 | FIRE EXTINGUISHERS |  |  |  |
| 4.8.1 | Supply and fix controlled discharge 9Kg carbon dioxide gas fire extinguisher manufactured to BS EN 3-9:2006, Bs 7863:2009, BS 5306- 4:2001 and the cylinder manufactured to BS 5045 complete with the following: Charge and fixing bracket, pictorial instructions, colour code, serviceable on site, discharge horn and hose, Brass hot stamping, Operating valve, local Fire Bridge approval. | No | 1 |  |
| 4.8.2 | Ditto but DRY powder fire extinguishers | No | 4 |  |
| 5 | SUBSTATION WORKS |  |  |  |
| 5.1 | Supply of Transformer and any other equipment Plinth including laying of ballast at the substation at least 100mm as per approved Design of Plant | SUM | 1 |  |
| 5.2 | Cable trenches |  |  |  |
| 5.2.1 | provide cable trenches (600x500) length approx. 100m at various Positions including HATARI slabs as per the approved layout | M | 100 |  |
| 6 | GENERATOR HOUSING |  |  |  |
| 6.1 | 5500mm long*4500mm wide Generator housing comprising of a stub masonry wall, mild steel grill comprising of 50*25*3mm RHS framings, vertical standards at 600mm centers, balusters size 20*20*3mm RHS at 150mm centers including welding and priming with red oxide, a double leaf mild steel door size 1500*3000mm and gauge 28 IT5 box profile roof. | SUM | 1 |  |
|  | TOTAL CARRIED TO GRAND SUMMARY |  |  |  |

| GRAND SUMMARY FOR CIVIL |  |  |
| --- | --- | --- |
| ITEM | DESCRIPTION | AMOUNT (KSH) |
| 1 | Chain Link Fence |  |
| 2 | Guard House |  |
| 3 | 2 door pit latrine |  |
| 4 | Container Office, Equipment Room, Substation Works, Storm Water, Drainage, Water Supply, Fire Protection & Access Road |  |
| SUB TOTAL |  |  |
| ADD 16% VAT |  |  |
| SUBTOTAL |  |  |
| GRAND TOTAL for Civil works (Item 1) |  |  |

- BILL OF QUANTITIES AND PRICE SCHEDULE FOR STEP UP SUBSTATION

| Item | Description | Unit | Qty | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- |
|  | CURRENCY: |  |  |  |  |
| 1 | Control Panels (Set with 1 Incomer and 1 Feeder) as per the requirement. | Set | 1 |  |  |
| 2 | Energy Meter (Tariff type, 415V three phase meter) For Feeder | No. | 1 |  |  |
| 3 | Cabling and Earthing for the step-up transformer and the outdoor equipment. The Transformer will be approximately 35 meters from the control room. (Cable size 240mm sq) and associated cable tray or trenches. Control Panels will be placed inside the inverter room. The bidder will provide all control and power cables for all equipment’s | No. | 1 |  |  |
| 4 | Step-up transformer 315 KVA, 0.415/11 KV Step-up TX, fitted with Buchholz relay, and pressure relief valve (See specs) | No. | 1 |  |  |
| 5 | 11 KV Circuit Breaker (Triple Pole) complete with outdoor Control and Protective relay panel and its accessories | No. | 1 |  |  |
| 6 | Outdoor Neutral current transformer (NCT) as per the requirement | No. | 1 |  |  |
| 7 | 11Kv Outdoor Current Transformers (CT) as per the requirement | No. | 3 |  |  |
| 8 | 11Kv Outdoor Voltage Transformers (VT) as per the requirement | No. | 3 |  |  |
| 9 | 11kv Lighting Arrester (LA)/ Surge Diverters | No. | 3 |  |  |
| 10 | 11Kv Isolator without Earth Switch (DS) | Set | 1 |  |  |
| 11 | 11Kv Isolator with Earth Switch (DSE) | Set | 1 |  |  |
| 12 | Mounting Structures for CT, VT, LA, DS and DSE | Set | 1 |  |  |
| 13 | 110VDC battery Bank supply | Set | 1 |  |  |
| 14 | 110VDC, 100AH Battery Charger | Set | 1 |  |  |
| 15 | Laptop computer fully loaded with the relays software initially stated in the specs. | Lot | 1 |  |  |
|  | SUB-TOTAL |  |  |  |  |
|  | ADD 16% VAT |  |  |  |  |
|  | TOTAL COST |  |  |  |  |

- 60 KWp SOLAR PV SYSTEM

| Item | Description | Unit | Qty | Unit Price | Total |
| --- | --- | --- | --- | --- | --- |
|  | Supply of Solar PV modules with junction box , Bypass Diodes, cable and MC4 connecter for inter connection with other module along with galvanized steel nuts & bolts for fixing up with module mounting structure as per the requirement & technical specification | KWp | 60 |  |  |
|  | Supply of hot dip galvanized MS steel/Aluminum Anodized made module-mounting structures(MMS) for above Modules of 60KWp capacity for holding modules including all necessary nuts and bolts as well as necessary clamps, foundations bolts etc. as per requirements and technical specifications and duly approved design by REREC | Lot | 1 |  |  |
|  | Supply of 600/1000v DC Distribution Board for Power distribution /Accumulation at DC side with MCBS/MCCBS protection system/Surge protection System | Lot | 1 |  |  |
|  | Supply, and installation of 20kW Hybrid Inverters, for conversion of Solar generation along with all protections and controlling arrangement for integration with BESS and DG along with AC Distribution Board for accumulation on AC side and equipment for remote monitoring facilities as per the requirement & technical specification. | No | 3 |  |  |
|  | Supply and install a 3-phase 60KVA power output diesel generator with 415 V at 50 Hz. It should include a highly corrosion resistant enclosure, control panel and monitoring, fuel tank and circuit breaker protection. The diesel generator shall be suitable for indoor or outdoor installation and shall perform accordingly with the battery inverter and the system design. The diesel generator shall work in a fully automatic manner with the above stated component | Set | 1 |  |  |
|  | Supply of at least 181KWh minimum Lithium-ion Battery Conforming to IEC62619 standard applicable to battery technology, Long life (10 years minimum) Complete in all respect and conforming to Requirement & technical specifications. All these enclosed in standard 40 feet steel container with ready to use air- conditioned battery room. | KWh | 181 |  |  |
|  | Cabling complete with all necessary accessories for connection of solar modules to battery bank, inverter, to intelligent controller/manager and to agreed connection point at the station through an energy meter and generator to the battery bank. This to also include cabling from the diesel generator for integration with power from the solar plant. | Lot | 1 |  |  |
|  | Supply of galvanized steel trays for cabling installation including all necessary nuts and bolts for Installation as per requirement of approved design as per Employer’s requirements and Technical specification | Lot | 1 |  |  |
|  | Supply of Early Streamer Emissions (E S E) Terminals with fulfilment of Standards UNE21186 and NF c 17102 to protect the arrays yard area and buildings against lightning protection as per approved design along with clamps and masts of requisite height. | Lot | 1 |  |  |
|  | Supply and install SCADA along all associated equipment, Data acquisition, data logger, Display Unit and industrial type PC with remote data monitoring. | Lot | 1 |  |  |
|  | Supply and install Weather monitoring system to check solar irradiation, wind speed and ambient temperature and integrate it with SCADA system. | Lot | 1 |  |  |
|  | Supply and install Security equipment including IP night vision 4 no’s Long vision Telescopic Closed Circuit Television (CCTV),IR motion sensors and 2 no’s short vision camera CCTV cameras with Video display at the control room | Lot | 1 |  |  |
|  | Laptop computer fully loaded with software for remote monitoring(to be use by REREC to monitor solar plant) | No | 1 |  |  |
|  | Sub-Total(Non Vatable Materials) |  |  |  |  |
|  | Sub-Total(Vatable Materials) |  |  |  |  |
|  | ADD 16% VAT (Only goods that attract VAT) |  |  |  |  |
|  | Total Cost For Solar Plant |  |  |  |  |

- Tools and Critical spares

| Item | Description | Unit | Qty | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- |
|  | Tools |  |  |  |  |
| 1 | Electrical Workshop 55+ Piece Inlay Tool Set with case | No | 1 |  |  |
| 2 | Mechanical Workshop 450+ Pieces (Cr-V) Drawer Tool Trolley (with plastic/foam modular inlay tool control system) –robust, sturdy and lockable. | No | 1 |  |  |
| 3 | Electric Hand Drill Chuck Capacity Of 1.5 – 13 Mm With Case | No | 1 |  |  |
| 4 | Angle Grinder 4 ½ ’’ with case | No | 1 |  |  |
| 5 | Electric Blower 800w | No | 1 |  |  |
| 6 | Electrical Digital Multi Meter | No | 2 |  |  |
| 7 | Electrical Clamp-On Meter | NO | 2 |  |  |
|  | Critical Spares |  |  |  |  |
| 1 | Fan belt | No | 2 |  |  |
| 2 | Air filter | No | 4 |  |  |
| 3 | Thermostat | No | 1 |  |  |
| 4 | Oil filter | No | 10 |  |  |
| 5 | Fuel filter | No | 10 |  |  |
| 6 | Engine Oil (litres) | No | 210 |  |  |
| 7 | Engine additive (litres) | No | 10 |  |  |
| 8 | Diodes set | No | I set |  |  |
| 9 | AVR | No | 1 |  |  |
| 10 | Electronic Fuel Control Units (Governor) | No | 1 |  |  |
|  | SUB-TOTAL |  |  |  |  |
|  | ADD 16% VAT (Only goods that attract VAT) |  |  |  |  |
| Total For Tools And Critical Spares |  |  |  |  |  |

- Services

| Item | Description | Unit | Qty | Unit Price | Total Price |
| --- | --- | --- | --- | --- | --- |
|  | Transport all to the station, installation, testing and commissioning of all equipment under supervision of REREC | Lot | 1 |  |  |
|  | Operation for 1 month inclusive of 1 month operator training. |  |  |  |  |
|  | 12 Months maintenance plus training of maintenance staff. | Lot | 1 |  |  |
|  | Factory acceptance test for the distribution board and outdoor Switchgear for 2 REREC/KPLC engineers. | Lot | 1 |  |  |
|  | Factory acceptance test for the transformer for 2 REREC/KPLC engineers. | Lot | 1 |  |  |
|  | Factory acceptance test for the Solar Modules for 2 REREC/KPLC engineers | Lot | 1 |  |  |
|  | Factory acceptance test for the Inverters for 2 REREC/KPLC engineers | Lot | 1 |  |  |
|  | Factory acceptance test for the lithium ion batteries for 2 REREC/KPLC engineers | Lot | 1 |  |  |
|  | Sub Total |  |  |  |  |
|  | Add 16% VAT |  |  |  |  |
|  | Total for Services |  |  |  |  |

| KIBWONGI ISLAND SOLAR POWER MINI GRID-LOT 2 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT |
| 1 | Total Civil Works, | Sum | 1 |  |  |
| 2 | Total Substation works | Sum | 1 |  |  |
| 3 | Total 60kW Solar Power Generation plant equipment | Sum | 1 |  |  |
| 4 | Tools and Critical spares | Sum | 1 |  |  |
| 5 | Total Services | Sum | 1 |  |  |
| 6 | 5% Contingency(to be used with the approval of the Project Manager) | Sum | 1 |  |  |
|  | TOTAL FOR KIBWONGI ISLAND SOLAR MINIGRID |  |  |  |  |

COST SUMMARY TO BE TRANSFERRED TO FORM OF TENDER AND ITEM TAB IN SRM SYSTEM

| KIWA AND KIBWONGI ISLAND SOLAR POWER MINI GRID |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT |
| 1 | Total for Kiwa island solar minigrid | Sum | 1 |  |  |
| 2 | Total for Kibwongi island solar minigrid | Sum | 1 |  |  |
|  | GRAND TOTAL |  |  |  |  |